## Inspections
Zone | Sub-Zone | Affiliate | Stations in ERIS | Inspector | Stations Assigned | Stations Inspected | COCO Inspected | CODO Inspected | Total CO inspected | DODO Inspected | Actions in Progress | Actions Closed | % Actions Closed
All | All | All | 4009 | All | 593 | 1716 | 16 | 1246 | 1262 | 454 | 10571 | 283 | 3%
AFR | MOI | TotalEnergies Marketing Tunisie | 153 | All | 62 | 62 | 0 | 28 | 28 | 34 | 150 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Tunisie | 153 | Bilel ABID | 36 | 36 | 0 | 8 | 8 | 28 | 24 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Tunisie | 153 | Meher BOUJELBENE | 13 | 13 | 0 | 7 | 7 | 6 | 0 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Tunisie | 153 | Ramzi DOGHMANE | 13 | 13 | 0 | 13 | 13 | 0 | 126 | 0 | 0%
AFR | ACE | TotalEnergies Marketing Malawi Ltd | 80 | All | 0 | 24 | 0 | 15 | 15 | 9 | 30 | 0 | 0%
AFR | ACE | TotalEnergies Marketing Malawi Ltd | 80 | NA | 24 | 24 | 0 | 15 | 15 | 9 | 30 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | All | 148 | 148 | 0 | 126 | 126 | 22 | 1949 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Abideen LAWAL | 13 | 13 | 0 | 8 | 8 | 5 | 116 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Adaji AGABI | 10 | 10 | 0 | 10 | 10 | 0 | 206 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Adegoke IBRAHIM | 17 | 17 | 0 | 7 | 7 | 10 | 178 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Babatunde ADEWUYI | 6 | 6 | 0 | 5 | 5 | 1 | 120 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Ben AMEH | 16 | 16 | 0 | 13 | 13 | 3 | 74 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Benjamin ADJOGBE | 16 | 16 | 0 | 16 | 16 | 0 | 141 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Davou ZANG | 4 | 4 | 0 | 4 | 4 | 0 | 11 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Félix EKPE | 8 | 8 | 0 | 8 | 8 | 0 | 77 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Femi-Samson SHOBAYO | 8 | 8 | 0 | 8 | 8 | 0 | 169 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Kazeem TAJUDEEN | 13 | 13 | 0 | 13 | 13 | 0 | 360 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Ojelade MARTINS | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Oluwasegun OYEBAMIJI | 3 | 3 | 0 | 3 | 3 | 0 | 10 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Oluwaseyi OYEWOLE | 8 | 8 | 0 | 8 | 8 | 0 | 196 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Stephen DELE-OSUNDE | 3 | 3 | 0 | 3 | 3 | 0 | 25 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Udeme OTUNG | 12 | 12 | 0 | 10 | 10 | 2 | 67 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Usivwin OHWONOHWO | 2 | 2 | 0 | 2 | 2 | 0 | 65 | 0 | 0%
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | 498 | Victor OKON | 8 | 8 | 0 | 7 | 7 | 1 | 134 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Gabon | 43 | All | 0 | 19 | 0 | 19 | 19 | 0 | 33 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Gabon | 43 | NA | 19 | 19 | 0 | 19 | 19 | 0 | 33 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Réunion | 43 | All | 0 | 28 | 0 | 18 | 18 | 10 | 82 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Réunion | 43 | NA | 28 | 28 | 0 | 18 | 18 | 10 | 82 | 0 | 0%
AFR | ACE | TotalEnergies Marketing Kenya PLC | 257 | All | 0 | 231 | 0 | 169 | 169 | 62 | 755 | 0 | 0%
AFR | ACE | TotalEnergies Marketing Kenya PLC | 257 | NA | 231 | 231 | 0 | 169 | 169 | 62 | 755 | 0 | 0%
AFR | ACE | TotalEnergies Marketing RDC S.A. | 44 | All | 42 | 42 | 0 | 39 | 39 | 3 | 55 | 0 | 0%
AFR | ACE | TotalEnergies Marketing RDC S.A. | 44 | Aimé MATONDO | 8 | 8 | 0 | 8 | 8 | 0 | 22 | 0 | 0%
AFR | ACE | TotalEnergies Marketing RDC S.A. | 44 | Christelle MABIALA | 5 | 5 | 0 | 5 | 5 | 0 | 0 | 0 | 0%
AFR | ACE | TotalEnergies Marketing RDC S.A. | 44 | Dany KANKU | 6 | 6 | 0 | 5 | 5 | 1 | 3 | 0 | 0%
AFR | ACE | TotalEnergies Marketing RDC S.A. | 44 | Diana KALAMBAY | 6 | 6 | 0 | 6 | 6 | 0 | 22 | 0 | 0%
AFR | ACE | TotalEnergies Marketing RDC S.A. | 44 | Roland BAKATUIPATA | 9 | 9 | 0 | 9 | 9 | 0 | 0 | 0 | 0%
AFR | ACE | TotalEnergies Marketing RDC S.A. | 44 | Vavi NZEZA | 8 | 8 | 0 | 6 | 6 | 2 | 8 | 0 | 0%
AFR | ACE | TotalEnergies Marketing Zambia Ltd | 67 | All | 0 | 6 | 0 | 4 | 4 | 2 | 22 | 0 | 0%
AFR | ACE | TotalEnergies Marketing Zambia Ltd | 67 | NA | 6 | 6 | 0 | 4 | 4 | 2 | 22 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Sénégal | 140 | All | 0 | 137 | 1 | 124 | 125 | 12 | 526 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Sénégal | 140 | NA | 137 | 137 | 1 | 124 | 125 | 12 | 526 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Moçambique SA | 82 | All | 0 | 38 | 1 | 26 | 27 | 11 | 444 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Moçambique SA | 82 | NA | 38 | 38 | 1 | 26 | 27 | 11 | 444 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | 73 | All | 0 | 12 | 0 | 12 | 12 | 0 | 123 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | 73 | NA | 12 | 12 | 0 | 12 | 12 | 0 | 123 | 0 | 0%
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | 108 | All | 0 | 26 | 0 | 23 | 23 | 3 | 485 | 0 | 0%
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | 108 | NA | 26 | 26 | 0 | 23 | 23 | 3 | 485 | 0 | 0%
AFR | ACE | TotalEnergies Marketing Uganda | 204 | All | 3 | 146 | 0 | 117 | 117 | 29 | 765 | 0 | 0%
AFR | ACE | TotalEnergies Marketing Uganda | 204 | NA | 146 | 146 | 0 | 117 | 117 | 29 | 765 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Cameroun S.A | 178 | All | 2 | 173 | 0 | 169 | 169 | 4 | 289 | 276 | 49%
AFR | AFO | TotalEnergies Marketing Cameroun S.A | 178 | NA | 174 | 173 | 0 | 169 | 169 | 4 | 289 | 276 | 49%
AFR | AFA | TotalEnergies Marketing Namibia Pty Ltd | 41 | All | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0%
AFR | AFA | TotalEnergies Marketing Namibia Pty Ltd | 41 | NA | 2 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0%
AFR | AFA | TotalEnergies Marketing South Africa | 519 | All | 147 | 147 | 0 | 92 | 92 | 55 | 427 | 1 | 0%
AFR | AFA | TotalEnergies Marketing South Africa | 519 | Khuliso NETSHIKHUDINI | 25 | 25 | 0 | 18 | 18 | 7 | 52 | 1 | 2%
AFR | AFA | TotalEnergies Marketing South Africa | 519 | Kurt GOVENDER | 30 | 30 | 0 | 4 | 4 | 26 | 0 | 0 | 0%
AFR | AFA | TotalEnergies Marketing South Africa | 519 | Lebokgang MOKOENA | 4 | 4 | 0 | 0 | 0 | 4 | 0 | 0 | 0%
AFR | AFA | TotalEnergies Marketing South Africa | 519 | Lethabo XINZI | 31 | 31 | 0 | 27 | 27 | 4 | 73 | 0 | 0%
AFR | AFA | TotalEnergies Marketing South Africa | 519 | Makalo KHOJANE | 5 | 5 | 0 | 3 | 3 | 2 | 19 | 0 | 0%
AFR | AFA | TotalEnergies Marketing South Africa | 519 | Mmapeu-Malucia MAKHAFOLA | 11 | 11 | 0 | 6 | 6 | 5 | 0 | 0 | 0%
AFR | AFA | TotalEnergies Marketing South Africa | 519 | Thivhonali NELWAMONDO | 5 | 5 | 0 | 5 | 5 | 0 | 0 | 0 | 0%
AFR | AFA | TotalEnergies Marketing South Africa | 519 | Vusi MSIZA | 36 | 36 | 0 | 29 | 29 | 7 | 283 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Guinée SA | 148 | All | 34 | 34 | 0 | 26 | 26 | 8 | 651 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Guinée SA | 148 | NA | 34 | 34 | 0 | 26 | 26 | 8 | 651 | 0 | 0%
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | 23 | All | 0 | 22 | 0 | 6 | 6 | 16 | 89 | 0 | 0%
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | 23 | NA | 22 | 22 | 0 | 6 | 6 | 16 | 89 | 0 | 0%
AFR | AFO | TOTAL PETROLEUM GHANA PLC | 271 | All | 126 | 126 | 0 | 73 | 73 | 53 | 1065 | 0 | 0%
AFR | AFO | TOTAL PETROLEUM GHANA PLC | 271 | Doris MINTA | 31 | 31 | 0 | 20 | 20 | 11 | 295 | 0 | 0%
AFR | AFO | TOTAL PETROLEUM GHANA PLC | 271 | Duncan TETTEY | 25 | 25 | 0 | 14 | 14 | 11 | 105 | 0 | 0%
AFR | AFO | TOTAL PETROLEUM GHANA PLC | 271 | Goddard AMISSAH | 17 | 17 | 0 | 16 | 16 | 1 | 297 | 0 | 0%
AFR | AFO | TOTAL PETROLEUM GHANA PLC | 271 | Mohammed OSUMANU | 22 | 22 | 0 | 10 | 10 | 12 | 155 | 0 | 0%
AFR | AFO | TOTAL PETROLEUM GHANA PLC | 271 | Vincent ATOMBOH | 31 | 31 | 0 | 13 | 13 | 18 | 213 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 170 | All | 0 | 45 | 1 | 42 | 43 | 2 | 727 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 170 | NA | 45 | 45 | 1 | 42 | 43 | 2 | 727 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Maroc | 389 | All | 0 | 124 | 9 | 15 | 24 | 100 | 91 | 6 | 6%
AFR | MOI | TotalEnergies Marketing Maroc | 389 | NA | 124 | 124 | 9 | 15 | 24 | 100 | 91 | 6 | 6%
AFR | ACE | TotalEnergies Marketing Zimbabwe | 94 | All | 0 | 51 | 3 | 46 | 49 | 2 | 569 | 0 | 0%
AFR | ACE | TotalEnergies Marketing Zimbabwe | 94 | NA | 51 | 51 | 3 | 46 | 49 | 2 | 569 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | 116 | All | 0 | 43 | 0 | 29 | 29 | 14 | 989 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | 116 | NA | 43 | 43 | 0 | 29 | 29 | 14 | 989 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Mauritius Ltd | 48 | All | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0%
AFR | MOI | TotalEnergies Marketing Mauritius Ltd | 48 | NA | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | 33 | All | 29 | 29 | 0 | 28 | 28 | 1 | 255 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | 33 | César EYI NGUEMA | 11 | 11 | 0 | 11 | 11 | 0 | 171 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | 33 | Ismael Leoncio ESONO | 10 | 10 | 0 | 9 | 9 | 1 | 18 | 0 | 0%
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | 33 | Óscar MITOGO | 8 | 8 | 0 | 8 | 8 | 0 | 66 | 0 | 0%

## Actions
Zone | Sub-Zone | Affiliate | Station Name | Station Code | Question Number | Question Text | Automated Action | Action completed (Y/N) | Action Valider | Deadline
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 28 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 28 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 28 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 28 Jan 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 28 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Airport View | KE111S0047 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Airport View | KE111S0047 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Airport View | KE111S0047 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Airport View | KE111S0047 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Airport View | KE111S0047 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Airport View | KE111S0047 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Airport View | KE111S0047 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Airport View | KE111S0047 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Airport View | KE111S0047 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Airport View | KE111S0047 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | E.11a | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | N |  | 26 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 26 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | F.02g | Are all LPG gas cylinders (full and empty) stored more than 3m away from vents and offloading coupling points? | Are all LPG gas cylinders (full and empty) stored more than 3m away from vents and offloading coupling points? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | F.02f | Are all gas cylinders (full and empty) more than 5m from the site's hydrocarbon tanks or dispensing equipment? | Are all gas cylinders (full and empty) more than 5m from the site's hydrocarbon tanks or dispensing equipment? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bahati | KE111S0051 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 30 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bahati | KE111S0051 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bahati | KE111S0051 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bahati | KE111S0051 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 30 Oct 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bahati | KE111S0051 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bahati | KE111S0051 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bahati | KE111S0051 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bahati | KE111S0051 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bahati | KE111S0051 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 30 Oct 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bahati | KE111S0051 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bamburi | KE411S0008 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 03 Aug 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bamburi | KE411S0008 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bamburi | KE411S0008 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bamburi | KE411S0008 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bamburi | KE411S0008 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 03 Aug 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bamburi | KE411S0008 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bamburi | KE411S0008 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bamburi | KE411S0008 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bamburi | KE411S0008 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Burnt Forest | KE111S0285 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 17 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Burnt Forest | KE111S0285 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 17 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Burnt Forest | KE111S0285 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 17 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Burnt Forest | KE111S0285 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Burnt Forest | KE111S0285 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Burnt Forest | KE111S0285 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Burnt Forest | KE111S0285 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Burnt Forest | KE111S0285 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Burnt Forest | KE111S0285 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 17 Aug 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Busia Road | KE111S0113 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Busia Road | KE111S0113 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Busia Road | KE111S0113 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Busia Road | KE111S0113 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker upstream of electrical installations. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Busia Road | KE111S0113 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Busia Road | KE111S0113 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Busia Road | KE111S0113 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Busia Road | KE111S0113 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Church Road | KE111S0043 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Church Road | KE111S0043 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Church Road | KE111S0043 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Church Road | KE111S0043 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Donholm | KE111S0182 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 09 Jan 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Eastern Bypass | KE111S0271 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Eastern Bypass | KE111S0271 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Eastern Bypass | KE111S0271 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Eastern Bypass | KE111S0271 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Eastern Bypass | KE111S0271 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Eastern Bypass | KE111S0271 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Eastern Bypass | KE111S0271 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Eastern Bypass | KE111S0271 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embu | KE111S0319 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embu | KE111S0319 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embu | KE111S0319 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gatitu | KE111S0007 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gatitu | KE111S0007 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gatitu | KE111S0007 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gatitu | KE111S0007 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gatitu | KE111S0007 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gatitu | KE111S0007 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gatitu | KE111S0007 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gilgil | KE111S0008 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 04 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gilgil | KE111S0008 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gilgil | KE111S0008 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gilgil | KE111S0008 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gilgil | KE111S0008 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gilgil | KE111S0008 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gilgil | KE111S0008 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gilgil | KE111S0008 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gilgil | KE111S0008 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 09 Feb 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 22 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 22 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 22 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 22 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 22 Jan 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 04 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Juja | KE111S0251 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 28 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Juja | KE111S0251 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Juja | KE111S0251 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 28 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Juja | KE111S0251 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Juja | KE111S0251 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Juja | KE111S0251 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Juja | KE111S0251 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Juja | KE111S0251 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Juja | KE111S0251 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kagwe | KE111S0012 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kagwe | KE111S0012 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kagwe | KE111S0012 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kagwe | KE111S0012 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kagwe | KE111S0012 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 28 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 28 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 28 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 28 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 28 Oct 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kamulu | KE111S0235 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kamulu | KE111S0235 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kamulu | KE111S0235 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 27 Dec 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kamulu | KE111S0235 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangundo Road | KE111S0123 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | E.11a | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | N |  | 14 Feb 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 14 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 14 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 14 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karambee | KE111S0062 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 16 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karambee | KE111S0062 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karambee | KE111S0062 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karambee | KE111S0062 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karambee | KE111S0062 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karambee | KE111S0062 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karambee | KE111S0062 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 16 Jan 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karatina | KE111S0163 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karatina | KE111S0163 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karatina | KE111S0163 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karatina | KE111S0163 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karatina | KE111S0163 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karatina | KE111S0163 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karatina | KE111S0163 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karatina | KE111S0163 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karatina | KE111S0163 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kariokor | KE111S0119 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kariokor | KE111S0119 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kariokor | KE111S0119 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kariokor | KE111S0119 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kariokor | KE111S0119 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 30 Jun 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kenyatta | KE111S0064 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kenyatta | KE111S0064 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kericho Star | KE111S0120 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 28 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kericho Star | KE111S0120 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 28 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kericho Star | KE111S0120 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 28 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kericho Star | KE111S0120 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kerugoya | KE111S0065 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 16 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kerugoya | KE111S0065 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kerugoya | KE111S0065 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kerugoya | KE111S0065 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kerugoya | KE111S0065 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kerugoya | KE111S0065 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kerugoya | KE111S0065 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kiambu | KE111S0121 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kiambu | KE111S0121 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kiambu | KE111S0121 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 12 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kiambu | KE111S0121 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kiambu | KE111S0121 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kiambu | KE111S0121 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 12 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kiambu | KE111S0121 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 12 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker upstream of electrical installations. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 14 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 14 May 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | D.26 | Are vent heads at least 4m high from the ground? | Raise vent heads to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 14 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 14 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 14 May 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kimende | KE111S0240 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kimende | KE111S0240 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kimende | KE111S0240 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kimende | KE111S0240 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kimende | KE111S0240 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 09 Aug 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kimende | KE111S0240 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kimende | KE111S0240 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 20 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 20 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 28 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 28 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 28 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 28 Aug 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | A.11b | If “YES”, is there a specific procedure for intervening near these power lines, and is it known by the station staff? | If “YES”, is there a specific procedure for intervening near these power lines, and is it known by the station staff? | N |  | 28 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 28 Aug 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 22 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 22 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 22 Jan 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Laikipia Road | KE111S0071 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Laikipia Road | KE111S0071 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Laikipia Road | KE111S0071 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Laikipia Road | KE111S0071 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Laikipia Road | KE111S0071 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Laikipia Road | KE111S0071 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Laikipia Road | KE111S0071 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Laikipia Road | KE111S0071 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Laikipia Road | KE111S0071 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Likoni Elf | KE111S0017 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Likoni Ferry | KE111S0125 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Likoni Ferry | KE111S0125 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Likoni Road | KE111S0126 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lumumba Avenue | KE111S0145 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 19 Jun 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lumumba Avenue | KE111S0145 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lumumba Avenue | KE111S0145 | G.07 | Is the service bay also used for car washing? | Is the service bay also used for car washing? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lumumba Avenue | KE111S0145 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lumumba Avenue | KE111S0145 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lumumba Avenue | KE111S0145 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 Sep 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lumumba Avenue | KE111S0145 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lusaka Road | KE111S0112 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 03 Aug 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 03 Aug 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 03 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 04 Jun 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 04 Dec 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mai Mahiu | KE111S0272 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mai Mahiu | KE111S0272 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 21 Dec 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Malindi Arcade | KE111S0129 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install Class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Malindi Arcade | KE111S0129 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Malindi Arcade | KE111S0129 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Malindi Arcade | KE111S0129 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 14 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mbagathi Road | KE111S0117 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mbagathi Road | KE111S0117 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mbagathi Road | KE111S0117 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 09 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 21 Jun 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 21 Sep 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 21 Sep 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha | KE111S0028 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha | KE111S0028 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 26 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha | KE111S0028 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha | KE111S0028 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha | KE111S0028 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha | KE111S0028 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha | KE111S0028 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha | KE111S0028 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha | KE111S0028 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha H/Way | KE111S0150 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 26 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha H/Way | KE111S0150 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha H/Way | KE111S0150 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha H/Way | KE111S0150 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha H/Way | KE111S0150 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha H/Way | KE111S0150 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha H/Way | KE111S0150 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha H/Way | KE111S0150 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha H/Way | KE111S0150 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nakuru Highway | KE111S0185 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nakuru Highway | KE111S0185 | F.02d | Are all LPG cylinders (full and empty) stored outside of the building? | Are all LPG cylinders (full and empty) stored outside of the building? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nakuru Highway | KE111S0185 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nakuru Highway | KE111S0185 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Plan to restore the gutters on the forecourt area. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | F.02d | Are all LPG cylinders (full and empty) stored outside of the building? | Are all LPG cylinders (full and empty) stored outside of the building? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 22 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nanyuki | KE111S0137 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 20 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nanyuki | KE111S0137 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nanyuki | KE111S0137 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nanyuki | KE111S0137 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nanyuki | KE111S0137 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nanyuki | KE111S0137 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naromoru | KE111S0030 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naromoru | KE111S0030 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 20 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naromoru | KE111S0030 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 01 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 01 Oct 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 01 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 01 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 01 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 01 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 01 Oct 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 01 Oct 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 01 Jan 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Gilgil | KE111S0128 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Gilgil | KE111S0128 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Gilgil | KE111S0128 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 04 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Gilgil | KE111S0128 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Gilgil | KE111S0128 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Gilgil | KE111S0128 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Isiolo | KE111S0160 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Isiolo | KE111S0160 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Isiolo | KE111S0160 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Isiolo | KE111S0160 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Isiolo | KE111S0160 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Isiolo | KE111S0160 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Isiolo | KE111S0160 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Isiolo | KE111S0160 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Isiolo | KE111S0160 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 03 Aug 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 03 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | J.01 | Does the station have a fire blanket? | Plan to install a fire blanket on the station. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Plan to restore the gutters on the forecourt area. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 13 Jun 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nkubu | KE111S0034 | G.07 | Is the service bay also used for car washing? | La baie de services est-elle également utilisée pour faire du lavage auto ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nkubu | KE111S0034 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 30 Mar 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | B.16 | Does the station have a general emergency stop button ? | Install a general emergency stop button for the station. | N |  | 30 Mar 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 30 Mar 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 30 Sep 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 30 Jun 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 10 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | C.11a | Is there a shovel in every sandbox? | Is there a shovel in every sandbox? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 28 Aug 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | F.02f | Are all gas cylinders (full and empty) more than 5m from the site's hydrocarbon tanks or dispensing equipment? | Are all gas cylinders (full and empty) more than 5m from the site's hydrocarbon tanks or dispensing equipment? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 28 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sotik | KE111S0037 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 05 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sotik | KE111S0037 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sotik | KE111S0037 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 05 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sotik | KE111S0037 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 05 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sotik | KE111S0037 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sotik | KE111S0037 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sotik | KE111S0037 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sotik | KE111S0037 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sotik | KE111S0037 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 22 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 22 Jul 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 22 Jan 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 07 Jun 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 07 Dec 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | C.12a | Are the seals of all the fire extinguishers intact? | Are the seals of all the fire extinguishers intact? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Tala | KE111S0147 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Tala | KE111S0147 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Tala | KE111S0147 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Tala | KE111S0147 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Tala | KE111S0147 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Temple Road | KE111S0089 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Temple Road | KE111S0089 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Temple Road | KE111S0089 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Temple Road | KE111S0089 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Temple Road | KE111S0089 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Temple Road | KE111S0089 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Temple Road | KE111S0089 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thika Highway | KE111S0167 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thika Highway | KE111S0167 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thika Highway | KE111S0167 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thika Highway | KE111S0167 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thika Highway | KE111S0167 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thika Highway | KE111S0167 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thika Highway | KE111S0167 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thika Highway | KE111S0167 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 14 Jun 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 14 Sep 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 14 Sep 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 14 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 14 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 14 May 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | H.01 | Is the flooring of the carwash areas non-slippery? | Is the flooring of the carwash areas non-slippery? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Wangige | KE111S0044 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Wangige | KE111S0044 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 12 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Wangige | KE111S0044 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 12 Nov 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Westend | KE111S0046 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Westend | KE111S0046 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Kenya PLC | Westend | KE111S0046 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Westend | KE111S0046 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 20 Dec 2025
AFR | ACE | TotalEnergies Marketing Kenya PLC | Westend | KE111S0046 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Westend | KE111S0046 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Westend | KE111S0046 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Kenya PLC | Westend | KE111S0046 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 15 Jul 2025
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 15 Jul 2025
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 15 Oct 2025
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 15 Jul 2025
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Plan to restore the gutters on the forecourt area. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 15 Oct 2025
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 15 Jan 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | 14e Rue | CD111S0066 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | 14e Rue | CD111S0066 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | 14e Rue | CD111S0066 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing RDC S.A. | 14e Rue | CD111S0066 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | 14e Rue | CD111S0066 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | 14e Rue | CD111S0066 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | 14e Rue | CD111S0066 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Badiadingi | CD111S0049 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Badiadingi | CD111S0049 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 19 Nov 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Badiadingi | CD111S0049 | D.23 | Is there a compliant pipe integrity test report available for this station? | Prévoir la réalisation d'une réépreuve acoustique des installations pétrolières du site. | N |  | 19 May 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Badiadingi | CD111S0049 | J.07 | Is the station connected to the public wastewater network (sewers)? | Prévoir une mise en conformité des eaux usées du site, selon l'Invariant ET03 | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing RDC S.A. | Benseke | CD111S0007 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Benseke | CD111S0007 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 19 Nov 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Benseke | CD111S0007 | J.07 | Is the station connected to the public wastewater network (sewers)? | Prévoir une mise en conformité des eaux usées du site, selon l'Invariant ET03 | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing RDC S.A. | Cadeco | CD111S0079 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Cadeco | CD111S0079 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 19 Nov 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Cadeco | CD111S0079 | D.23 | Is there a compliant pipe integrity test report available for this station? | Prévoir la réalisation d'une réépreuve acoustique des installations pétrolières du site. | N |  | 19 May 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Cadeco | CD111S0079 | J.07 | Is the station connected to the public wastewater network (sewers)? | Prévoir une mise en conformité des eaux usées du site, selon l'Invariant ET03 | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 26 Jun 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Une mesure de résistance de la mise à la terre des installations de la station est-elle bien indiquée dans ce rapport ? Et est-elle bien inférieure à 10 ohms ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | L'ensemble des équipements de la baie peut-il être neutralisé par un bouton d'arrêt d'urgence ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | D.16 | Does the station have a graduated gauge ruler in good condition, allowing manual gauging to be carried out? | Fournir une règle de jauge à la station. | N |  | 26 Jun 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | H.02 | Are carwash installations equipped with an emergency stop button? | Les installations de lavage sont-elles équipées d'un bouton d'arrêt d'urgence ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | G.20 | Is used oil collected and properly treated? | Les huiles usées sont-elles collectées et traitées correctement ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 26 Dec 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Marché | CD111S0033 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing RDC S.A. | Marché | CD111S0033 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Marché | CD111S0033 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 19 Nov 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Marché | CD111S0033 | D.23 | Is there a compliant pipe integrity test report available for this station? | Prévoir la réalisation d'une réépreuve acoustique des installations pétrolières du site. | N |  | 19 May 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Mayo | CD111S0071 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing RDC S.A. | Mayo | CD111S0071 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Mayo | CD111S0071 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 19 Nov 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Mayo | CD111S0071 | D.23 | Is there a compliant pipe integrity test report available for this station? | Prévoir la réalisation d'une réépreuve acoustique des installations pétrolières du site. | N |  | 19 May 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Moulaert | CD111S0023 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing RDC S.A. | Moulaert | CD111S0023 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation des détecteur de fuite de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing RDC S.A. | Moulaert | CD111S0023 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing RDC S.A. | Moulaert | CD111S0023 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Moulaert | CD111S0023 | D.19 | Does the station manager monitor fuel losses: WetStock Management? | L'exploitant a-t-il un suivi des pertes carburants : WetStock Management ? | N |  | 27 Jun 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Moulaert | CD111S0023 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing RDC S.A. | Moulaert | CD111S0023 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing RDC S.A. | Moulaert | CD111S0023 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 27 Dec 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Non Stop | CD111S0037 | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Non Stop | CD111S0037 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 24 Dec 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Ucc | CD111S0061 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Ucc | CD111S0061 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 19 Nov 2025
AFR | ACE | TotalEnergies Marketing RDC S.A. | Ucc | CD111S0061 | D.23 | Is there a compliant pipe integrity test report available for this station? | Prévoir la réalisation d'une réépreuve acoustique des installations pétrolières du site. | N |  | 19 May 2026
AFR | ACE | TotalEnergies Marketing RDC S.A. | Vangu | CD111S0011 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 07 Jan 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 27 Feb 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | C.11a | Is there a shovel in every sandbox? | Is there a shovel in every sandbox? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 05 Feb 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Clock Tower Gapco | TZ211S0015 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Clock Tower Gapco | TZ211S0015 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Clock Tower Gapco | TZ211S0015 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Clock Tower Gapco | TZ211S0015 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Clock Tower Gapco | TZ211S0015 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Clock Tower Gapco | TZ211S0015 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 27 Feb 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Kariakoo Gapco Star | TZ211S0018 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Kariakoo Gapco Star | TZ211S0018 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Kariakoo Gapco Star | TZ211S0018 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Kariakoo Gapco Star | TZ211S0018 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Kariakoo Gapco Star | TZ211S0018 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Kariakoo Gapco Star | TZ211S0018 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | J.01 | Does the station have a fire blanket? | Plan to install a fire blanket on the station. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 27 Feb 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Les bouches de dépotages sont-elles protégées à l'aide d'un musoir, d'un muret en béton ou de poteaux anti-bélier ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | C.11a | Is there a shovel in every sandbox? | Y a-t-il bien une pelle dans chaque bac à sable ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Prévoir la mise en place de têtes de jauge type "baïonnette" sur site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | H.02 | Are carwash installations equipped with an emergency stop button? | Les installations de lavage sont-elles équipées d'un bouton d'arrêt d'urgence ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 27 Feb 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation des détecteur de fuite de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Les portiques et autres équipements mobiles de lavage sont-ils tous correctement positionnés pour éviter tout risque d'écrasement en fonctionnement ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msimbazi | TZ211S0021 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msimbazi | TZ211S0021 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msimbazi | TZ211S0021 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msimbazi | TZ211S0021 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msimbazi | TZ211S0021 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msimbazi | TZ211S0021 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msimbazi | TZ211S0021 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton dedicated to the forecourt and instantly accessible by station staff. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | B.16b | Do station staff know where the emergency stop is located to cut off the fuel distribution power supply, and how to use it? | Make station staff aware of how to operate the forecourt emergency stop. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Adjust vent distance to make them visible from the offloading and comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Samora Gapco Star | TZ211S0009 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Samora Gapco Star | TZ211S0009 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Samora Gapco Star | TZ211S0009 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Samora Gapco Star | TZ211S0009 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Samora Gapco Star | TZ211S0009 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Samora Gapco Star | TZ211S0009 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Samora Gapco Star | TZ211S0009 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 27 Feb 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Faire réaliser une inspection complète des installations électriques du site par un bureau de contrôle agréé. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | E.06 | Are all the offloading coupling ports padlocked? | Les bouches de dépotage sont-elles toutes bien cadenassées ? | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | Si la baie est équipée de fosses, sont-elles toutes sécurisées à l'aide d'un caillebotis galvanisés ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.07 | Is the service bay also used for car washing? | La baie de services est-elle également utilisée pour faire du lavage auto ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | L'ensemble des équipements de la baie peut-il être neutralisé par un bouton d'arrêt d'urgence ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Les portiques et autres équipements mobiles de lavage sont-ils tous correctement positionnés pour éviter tout risque d'écrasement en fonctionnement ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 27 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 27 Feb 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 23 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 23 Nov 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 27 Feb 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton dedicated to the forecourt and instantly accessible by station staff. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | B.16b | Do station staff know where the emergency stop is located to cut off the fuel distribution power supply, and how to use it? | Make station staff aware of how to operate the forecourt emergency stop. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.09 | Are manual gauging/dipping heads easily accessible to the station staff (maximum 30 cm below forecourt road cover)? | Are manual gauging/dipping heads easily accessible to the station staff (maximum 30 cm below forecourt road cover)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | J.01 | Does the station have a fire blanket? | Plan to install a fire blanket on the station. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 27 Aug 2025
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bakuli | UG111S2236 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bakuli | UG111S2236 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bakuli | UG111S2236 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bakuli | UG111S2236 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bombo | UG111S2269 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bombo | UG111S2269 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bombo | UG111S2269 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Bombo | UG111S2269 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bombo | UG111S2269 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bombo | UG111S2269 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bombo | UG111S2269 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bombo | UG111S2269 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 10 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 10 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bukoto | UG111S2239 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bukoto | UG111S2239 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Bukoto | UG111S2239 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bukoto | UG111S2239 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bukoto | UG111S2239 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 30 Jun 2025
AFR | ACE | TotalEnergies Marketing Uganda | Bukoto | UG111S2239 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bukoto | UG111S2239 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bukoto | UG111S2239 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bukoto | UG111S2239 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 08 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 08 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise | UG111S2260 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise | UG111S2260 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise | UG111S2260 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise | UG111S2260 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise | UG111S2260 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise | UG111S2260 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise | UG111S2260 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise | UG111S2260 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise | UG111S2260 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise | UG111S2260 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 08 Aug 2025
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | City centre | UG111S2276 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | City centre | UG111S2276 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | City centre | UG111S2276 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 14 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | City centre | UG111S2276 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | City centre | UG111S2276 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 14 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | City centre | UG111S2276 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | City centre | UG111S2276 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | City centre | UG111S2276 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 08 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 08 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Gayaza Rd | UG111S2242 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Gayaza Rd | UG111S2242 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Gayaza Rd | UG111S2242 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Gayaza Rd | UG111S2242 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Gayaza Rd | UG111S2242 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Gayaza Rd | UG111S2242 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Gayaza Rd | UG111S2242 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 04 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 04 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 20 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 20 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 25 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 25 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main | UG111S2282 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main | UG111S2282 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main | UG111S2282 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main | UG111S2282 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main | UG111S2282 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main | UG111S2282 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main | UG111S2282 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main Street | UG111S2222 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main Street | UG111S2222 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main Street | UG111S2222 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main Street | UG111S2222 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main Street | UG111S2222 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main Street | UG111S2222 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kalerwe | UG111S2286 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 14 Jul 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kalerwe | UG111S2286 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kalerwe | UG111S2286 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kalerwe | UG111S2286 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kalerwe | UG111S2286 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 14 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 14 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 03 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 03 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 03 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 03 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 10 Jul 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kibuli | UG111S2248 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kibuli | UG111S2248 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Kibuli | UG111S2248 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kibuli | UG111S2248 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kibuli | UG111S2248 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kibuli | UG111S2248 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kibuli | UG111S2248 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kibuli | UG111S2248 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kibuli | UG111S2248 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 24 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 24 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 23 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 23 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 10 Jul 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 17 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 17 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 28 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 28 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera ward | UG111S2375 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera ward | UG111S2375 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera ward | UG111S2375 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera ward | UG111S2375 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera ward | UG111S2375 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera ward | UG111S2375 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera ward | UG111S2375 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera ward | UG111S2375 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Lira | UG111S2249 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Lira | UG111S2249 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Lira | UG111S2249 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Lira | UG111S2249 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Lira | UG111S2249 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Lira | UG111S2249 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Lira | UG111S2249 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Plan to bring the bay's water treatment back into compliance with Invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Lugazi | UG111S2301 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Lugazi | UG111S2301 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Lugazi | UG111S2301 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Lugazi | UG111S2301 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Lugazi | UG111S2301 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Lugazi | UG111S2301 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Lugazi | UG111S2301 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Lugazi | UG111S2301 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton dedicated to the forecourt and instantly accessible by station staff. | N |  | 24 Jul 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 24 Jul 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 24 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 24 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 22 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Adjust vent distance to make them visible from the offloading and comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | F.02g | Are all LPG gas cylinders (full and empty) stored more than 3m away from vents and offloading coupling points? | Are all LPG gas cylinders (full and empty) stored more than 3m away from vents and offloading coupling points? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | F.02f | Are all gas cylinders (full and empty) more than 5m from the site's hydrocarbon tanks or dispensing equipment? | Are all gas cylinders (full and empty) more than 5m from the site's hydrocarbon tanks or dispensing equipment? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 24 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 24 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 23 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 23 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 23 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 23 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 11 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 11 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 11 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 11 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton dedicated to the forecourt and instantly accessible by station staff. | N |  | 23 Jul 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 23 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 23 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 09 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 09 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Najjera 2 | UG111S2456 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Najjera 2 | UG111S2456 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Najjera 2 | UG111S2456 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Najjera 2 | UG111S2456 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Najjera 2 | UG111S2456 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Najjera 2 | UG111S2456 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 08 May 2025
AFR | ACE | TotalEnergies Marketing Uganda | Najjera 2 | UG111S2456 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Najjera 2 | UG111S2456 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Najjera 2 | UG111S2456 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Najjera 2 | UG111S2456 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 18 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 18 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nakavule | UG111S2366 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton dedicated to the forecourt and instantly accessible by station staff. | N |  | 30 Jun 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nakavule | UG111S2366 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Nakavule | UG111S2366 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakavule | UG111S2366 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 30 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nakavule | UG111S2366 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakavule | UG111S2366 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakavule | UG111S2366 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 30 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nakavule | UG111S2366 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 26 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 26 Sep 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 14 Jul 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 14 Jul 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 15 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 15 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 04 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 04 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 23 Jul 2025
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Provide concrete blocks on islands to protect dispensers from crashes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 23 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 23 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 10 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 10 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 10 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 10 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | C.11a | Is there a shovel in every sandbox? | Is there a shovel in every sandbox? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 16 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 16 Oct 2025
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Avondale | ZM111S2284 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Avondale | ZM111S2284 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Avondale | ZM111S2284 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Avondale | ZM111S2284 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Avondale | ZM111S2284 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chilenje | ZM111S2217 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chilenje | ZM111S2217 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tank compartments on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chilenje | ZM111S2217 | D.06 | Are all the station's fuel tanks double-walled? | Plan for the replacement of the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chilenje | ZM111S2217 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chilenje | ZM111S2217 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chilenje | ZM111S2217 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chingola A | ZM111S2203 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chingola A | ZM111S2203 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chingola A | ZM111S2203 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chingola A | ZM111S2203 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chingola A | ZM111S2203 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chingola A | ZM111S2203 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chipata | ZM111S4201 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chipata | ZM111S4201 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chipata | ZM111S4201 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chipata | ZM111S4201 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chipata | ZM111S4201 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | 12th Avenue | ZW111S0006 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | 12th Avenue | ZW111S0006 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | 13th Avenue | ZW111S0004 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | 13th Avenue | ZW111S0004 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | 4th Avenue | ZW111S0011 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | 4th Avenue | ZW111S0011 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tank compartments on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading area into compliance with the Invariant EP10. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.06 | Are all the station's fuel tanks double-walled? | Plan for the replacement of the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | E.03 | Is the offloading area oil-tight? | Plan to make the offloading area compliant with Invariant ET04. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Amc Kariba | ZW111S0065 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Amc Kariba | ZW111S0065 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 18 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Amc Kariba | ZW111S0065 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Amc Kariba | ZW111S0065 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Amc Kariba | ZW111S0065 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Amc Kariba | ZW111S0065 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Amc Kariba | ZW111S0065 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Amc Kariba | ZW111S0065 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Ascot | ZW111S0001 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Ascot | ZW111S0001 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Ascot | ZW111S0001 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Ascot | ZW111S0001 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Ascot | ZW111S0001 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Install PLLD (Pressurized Line Leak Detector) pressure sensors on all submersible pumps on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.02l | Is the automatic gauging system interconnected to the dispensers to enable stock reconciliation and continuous leak detection? | Plan to install the dedicated management module in the automatic gauge. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are ALL the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Implement the LockOut - TagOut procedures for the maintenance of pressurized sites and inform the station staff. | N |  | 05 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 automatic gauge on the station. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 24 Dec 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Belmont | ZW111S0010 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Belmont | ZW111S0010 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Belmont | ZW111S0010 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Budiriro | ZW111S0061 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Budiriro | ZW111S0061 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Budiriro | ZW111S0061 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Budiriro | ZW111S0061 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Budiriro | ZW111S0061 | D.28 | Are the vents more than 3 meters from an electrical source? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Budiriro | ZW111S0061 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Budiriro | ZW111S0061 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 07 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Budiriro | ZW111S0061 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 07 Feb 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chinhoyi Street | ZW111S0043 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chinhoyi Street | ZW111S0043 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chinhoyi Street | ZW111S0043 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chinhoyi Street | ZW111S0043 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chinhoyi Street | ZW111S0043 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chinhoyi Street | ZW111S0043 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chinhoyi Street | ZW111S0043 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chinhoyi Street | ZW111S0043 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chirundu | ZW111S0084 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 17 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chirundu | ZW111S0084 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chirundu | ZW111S0084 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chirundu | ZW111S0084 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chirundu | ZW111S0084 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chirundu | ZW111S0084 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 20 Sep 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 20 Dec 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 20 Dec 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Emerald Hill | ZW111S0042 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Emerald Hill | ZW111S0042 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 14 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Emerald Hill | ZW111S0042 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Emerald Hill | ZW111S0042 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Emerald Hill | ZW111S0042 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Emerald Hill | ZW111S0042 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Emerald Hill | ZW111S0042 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 14 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Emerald Hill | ZW111S0042 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 14 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Entumbane | ZW111S0012 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Entumbane | ZW111S0012 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Entumbane | ZW111S0012 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 17 Jul 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Entumbane | ZW111S0012 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Entumbane | ZW111S0012 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Fife Street | ZW111S0013 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Fife Street | ZW111S0013 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Fife Street | ZW111S0013 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Fife Street | ZW111S0013 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Fort Street | ZW111S0007 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Fort Street | ZW111S0007 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 07 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 07 Feb 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Hillcrest | ZW111S0014 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Hillcrest | ZW111S0014 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Hillcrest | ZW111S0014 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Hillcrest | ZW111S0014 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Karoi | ZW111S0085 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tank compartments on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 15 May 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading area into compliance with the Invariant EP10. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.06 | Are all the station's fuel tanks double-walled? | Plan for the replacement of the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 15 May 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 24 Sep 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 24 Dec 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tank compartments on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 15 May 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Adjust vent distance to make them visible from the offloading and comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading area into compliance with the Invariant EP10. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.06 | Are all the station's fuel tanks double-walled? | Plan for the replacement of the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 15 May 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 20 Sep 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Mazowe | ZW111S0053 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tank compartments on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading area into compliance with the Invariant EP10. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.06 | Are all the station's fuel tanks double-walled? | Plan for the replacement of the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 24 Dec 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Nelson Mandela | ZW111S0032 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Nelson Mandela | ZW111S0032 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Nelson Mandela | ZW111S0032 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 13 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Nelson Mandela | ZW111S0032 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Nelson Mandela | ZW111S0032 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Nelson Mandela | ZW111S0032 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Nelson Mandela | ZW111S0032 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 09 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 09 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 09 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 09 Feb 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Plumtree | ZW111S0015 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Plumtree | ZW111S0015 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Plumtree | ZW111S0015 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | R G Mugabe 2 | ZW111S0005 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape | ZW111S0019 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape | ZW111S0019 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape | ZW111S0019 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape | ZW111S0019 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape | ZW111S0019 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape | ZW111S0019 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 05 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape | ZW111S0019 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape | ZW111S0019 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 05 Feb 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape 2 | ZW111S0024 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape 2 | ZW111S0024 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape 2 | ZW111S0024 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape 2 | ZW111S0024 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape 2 | ZW111S0024 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape 2 | ZW111S0024 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 05 Feb 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 07 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 07 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 20 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | B.16 | Does the station have a general emergency stop button ? | Install a general emergency stop button for the station. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 24 Dec 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 24 Jun 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 24 Dec 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Southworld | ZW111S0017 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Southworld | ZW111S0017 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Southworld | ZW111S0017 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | N |  | 07 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 05 Aug 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 05 Feb 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | ACE | TotalEnergies Marketing Zimbabwe | Westgate | ZW111S0155 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 15 Nov 2025
AFR | ACE | TotalEnergies Marketing Zimbabwe | Westgate | ZW111S0155 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | ACE | TotalEnergies Marketing Zimbabwe | Westgate | ZW111S0155 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | ACE | TotalEnergies Marketing Zimbabwe | Westgate | ZW111S0155 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 15 Nov 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | C.11a | Is there a shovel in every sandbox? | Is there a shovel in every sandbox? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 26 May 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 26 Aug 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 26 Feb 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 26 Feb 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 26 Feb 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | J.03 | Does the station have a first-aid kit? | Does the station have a first-aid kit? | N |  | 26 Feb 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 26 Feb 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 26 May 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Hub | SZ111S0002 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Hub | SZ111S0002 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Hub | SZ111S0002 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Hub | SZ111S0002 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 04 Jun 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 04 Jun 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 04 Jun 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | E.11a | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | N |  | 04 Jun 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | N |  | 04 Jun 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 04 Jun 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 04 Jun 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Moneni | SZ111S0007 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Moneni | SZ111S0007 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Moneni | SZ111S0007 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Moneni | SZ111S0007 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 28 Sep 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Moneni | SZ111S0007 | C.12 | Is the forecourt equipped with one ABC powder extinguisher per island? | Provide one ABC extinguisher per forecourt distribution island. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Moneni | SZ111S0007 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 27 Mar 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 27 Mar 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | C.11b | Do all the sand boxes have a lid / cover? | Do all the sand boxes have a lid / cover? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | C.11c | Is the sand clean and free of waste in all sandboxes | Is the sand clean and free of waste in all sandboxes | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | D.28 | Are the vents more than 3 meters from an electrical source? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | J.01 | Does the station have a fire blanket? | Plan to install a fire blanket on the station. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 27 Jun 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Mar 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | C.11a | Is there a shovel in every sandbox? | Is there a shovel in every sandbox? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 27 Jun 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 27 Sep 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 28 Feb 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 28 Feb 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | J.01 | Does the station have a fire blanket? | Plan to install a fire blanket on the station. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Does the station have showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 28 Feb 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 28 May 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 28 Feb 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 28 Feb 2025
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 28 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 28 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 28 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 28 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 28 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 28 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | C.11c | Is the sand clean and free of waste in all sandboxes | Is the sand clean and free of waste in all sandboxes | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Adjust vent distance to make them visible from the offloading and comply with invariant EP09. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Plan to install a wastewater treatment system in accordance with invariant ET03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 28 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 28 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 21 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 21 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | C.11a | Is there a shovel in every sandbox? | Is there a shovel in every sandbox? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 21 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Adjust vent distance to make them visible from the offloading and comply with invariant EP09. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 21 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 13 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | J.01 | Does the station have a fire blanket? | Plan to install a fire blanket on the station. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 13 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 13 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 09 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 09 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | E.11a | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | N |  | 09 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 09 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 23 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Plan to restore the gutters on the forecourt area. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 23 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 23 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Marylone | ZA111S0060 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 16 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Marylone | ZA111S0060 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Marylone | ZA111S0060 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 16 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Marylone | ZA111S0060 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Marylone | ZA111S0060 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Marylone | ZA111S0060 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 16 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Melkbos | ZA111S0238 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Melkbos | ZA111S0238 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 21 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Melkbos | ZA111S0238 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Melkbos | ZA111S0238 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Melkbos | ZA111S0238 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Melkbos | ZA111S0238 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Melkbos | ZA111S0238 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Melkbos | ZA111S0238 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 21 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Melkbos | ZA111S0238 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Melkbos | ZA111S0238 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 14 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 14 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 14 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 14 May 2026
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 14 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 14 May 2026
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | Y | Khuliso NETSHIKHUDINI | 08 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 08 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 08 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 08 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 08 Oct 2025
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 08 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 25 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | J.01 | Does the station have a fire blanket? | Plan to install a fire blanket on the station. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 25 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 25 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 25 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 25 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 18 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 18 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 18 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 14 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 14 May 2026
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 14 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 14 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 14 May 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarden Eiland | ZA111S0522 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Paarden Eiland | ZA111S0522 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarden Eiland | ZA111S0522 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Paarden Eiland | ZA111S0522 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarden Eiland | ZA111S0522 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 21 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarden Eiland | ZA111S0522 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Paarden Eiland | ZA111S0522 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 18 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are ALL the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Implement the LockOut - TagOut procedures for the maintenance of pressurized sites and inform the station staff. | N |  | 18 Oct 2025
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 18 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 18 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Parklands | ZA111S0254 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Parklands | ZA111S0254 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Parklands | ZA111S0254 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Parklands | ZA111S0254 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Parklands | ZA111S0254 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Parklands | ZA111S0254 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Parklands | ZA111S0254 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Parklands | ZA111S0254 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Parklands | ZA111S0254 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 25 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria North | ZA111S0070 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria North | ZA111S0070 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 01 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria North | ZA111S0070 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 01 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria North | ZA111S0070 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria North | ZA111S0070 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria North | ZA111S0070 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria North | ZA111S0070 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria North | ZA111S0070 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 01 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria South | ZA111S0071 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 17 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria South | ZA111S0071 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria South | ZA111S0071 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria South | ZA111S0071 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria South | ZA111S0071 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria South | ZA111S0071 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 17 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria South | ZA111S0071 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 17 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria South | ZA111S0071 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria South | ZA111S0071 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria South | ZA111S0071 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Petroport Piketberg | ZA111S0286 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Petroport Piketberg | ZA111S0286 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Petroport Piketberg | ZA111S0286 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 30 Dec 2025
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 14 Nov 2025
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 14 May 2026
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 14 May 2026
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 15 May 2026
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 15 May 2026
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 02 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 02 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 02 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 02 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Plan to restore the gutters on the forecourt area. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 18 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are ALL the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Implement the LockOut - TagOut procedures for the maintenance of pressurized sites and inform the station staff. | N |  | 18 Oct 2025
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 18 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.02p | Are prefabricated PE oiltight sumps installed below all dispensers on the pressurized site ? | Plan to install prefabricated PE oiltight sumps below all dispensers on the pressurized site. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Strand | ZA111S0272 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Strand | ZA111S0272 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Strand | ZA111S0272 | H.01 | Is the flooring of the carwash areas non-slippery? | Is the flooring of the carwash areas non-slippery? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Strand | ZA111S0272 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 18 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Strand | ZA111S0272 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFA | TotalEnergies Marketing South Africa | Strand | ZA111S0272 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Strand | ZA111S0272 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Strand | ZA111S0272 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 18 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Strand | ZA111S0272 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Sunningdale | ZA111S0955 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Sunningdale | ZA111S0955 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Sunningdale | ZA111S0955 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Sunningdale | ZA111S0955 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Sunningdale | ZA111S0955 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Sunningdale | ZA111S0955 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Sunningdale | ZA111S0955 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 21 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Sunningdale | ZA111S0955 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Sunningdale | ZA111S0955 | H.04 | Is the lighting of washing areas sufficient and operational? | Plan to revamp the lighting in the carwash area. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Sunningdale | ZA111S0955 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 23 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 23 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Implement the LockOut - TagOut procedures for the maintenance of pressurized sites and inform the station staff. | N |  | 23 Oct 2025
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 23 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 18 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 18 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 18 Jan 2026
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 18 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 18 Jul 2025
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Waltloo | ZA111S0023 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Waltloo | ZA111S0023 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFA | TotalEnergies Marketing South Africa | Waltloo | ZA111S0023 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | AFA | TotalEnergies Marketing South Africa | Waltloo | ZA111S0023 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | 37 Hospital Road | GH111S0001 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | 37 Hospital Road | GH111S0001 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 12 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 12 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 23 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 23 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 23 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 23 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | C.15 | Is the forecourt operated without supervision: no pump attendant and no visibility from the cashier desk, or unmanned night opening with OPT or 100% automated station? | Is the forecourt operated without supervision: no pump attendant and no visibility from the cashier desk, or unmanned night opening with OPT or 100% automated station? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.16 | Does the station have a graduated gauge ruler in good condition, allowing manual gauging to be carried out? | Provide a gauging ruler to the station. | N |  | 23 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.28 | Are the vents more than 3 meters from an electrical source? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 23 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 23 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | C.15a | If "YES", is the site equipped with an emergency call system connected to a remote monitoring center or to a person designated and trained to handle incidents? | Plan to comply with invariant ES08 on unsupervised forecourt. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 23 Oct 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 23 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 23 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | La station fonctionne-t-elle en refoulement, avec des pompes immergées situées au niveau des plateaux trou-d'homme des réservoirs carburants ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.02b | Does the affiliate have a specific system for monitoring, justifying and tracing fuel losses at service stations in writing?" | Prévoir la mise en place d'un organisation spécifique au suivi des pertes carburant en station. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.02e | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | Ce contrat de maintenance prévoit-il une mise en sécurité des installations en refoulement 24h/24 si besoin ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 23 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 23 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Prévoir l'installations de capteurs de pressions PLLD (Pressurized Line Leak Detector) sur toutes les pompes immergées du site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 25 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 25 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | B.16b | Do station staff know where the emergency stop is located to cut off the fuel distribution power supply, and how to use it? | Make station staff aware of how to operate the forecourt emergency stop. | N |  | 25 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 25 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 28 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 28 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 28 Oct 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 28 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 28 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | D.04b | If “NO”, are these above-ground tanks double-walled? | If “NO”, are these above-ground tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aflao | GH111S0013 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 27 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aflao | GH111S0013 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aflao | GH111S0013 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aflao | GH111S0013 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aflao | GH111S0013 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aflao | GH111S0013 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aflao | GH111S0013 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aflao | GH111S0013 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aflao | GH111S0013 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akim Oda | GH111S0020 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 27 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akim Oda | GH111S0020 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akim Oda | GH111S0020 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akim Oda | GH111S0020 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akim Oda | GH111S0020 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akpokple | GH111S0022 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akpokple | GH111S0022 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akpokple | GH111S0022 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akpokple | GH111S0022 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akpokple | GH111S0022 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 24 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 24 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 24 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 24 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 08 Aug 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | H.01 | Is the flooring of the carwash areas non-slippery? | Is the flooring of the carwash areas non-slippery? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 08 Nov 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 08 Feb 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 10 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 10 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 10 Jan 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 09 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 09 Jan 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 15 Oct 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Plan to restore the gutters on the forecourt area. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 15 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | K.15 | Are PV inverters installed in a place that is inaccessible to the public, and protected from rain and UV rays? | Protect and secure the site's photovoltaic installations. | N |  | 15 Jan 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 15 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 26 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 26 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Adjust vent distance to make them visible from the offloading and comply with invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 26 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 26 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 26 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 26 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 26 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 26 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 26 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 26 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 26 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Buipe | GH111S0286 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Buipe | GH111S0286 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Buipe | GH111S0286 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Buipe | GH111S0286 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Buipe | GH111S0286 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Buipe | GH111S0286 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Buipe | GH111S0286 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Buipe | GH111S0286 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Buipe | GH111S0286 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Buipe | GH111S0286 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 25 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 25 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 08 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 08 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 08 Jan 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Community 1 Market | GH111S0066 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 07 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Community 1 Market | GH111S0066 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Community 1 Market | GH111S0066 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Community 1 Market | GH111S0066 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Community 1 Market | GH111S0066 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Community 1 Market | GH111S0066 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Community 1 Market | GH111S0066 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Community 1 Market | GH111S0066 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Community 1 Market | GH111S0066 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Community 1 Market | GH111S0066 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 27 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | B.16b | Do station staff know where the emergency stop is located to cut off the fuel distribution power supply, and how to use it? | Make station staff aware of how to operate the forecourt emergency stop. | N |  | 27 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 27 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 22 Oct 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 22 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 22 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 22 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 22 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 22 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 25 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 25 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 25 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 25 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 25 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 25 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 17 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 17 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 17 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Gopdc Kwae | GH111S0087 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 18 May 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Gopdc Kwae | GH111S0087 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Gopdc Kwae | GH111S0087 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Gopdc Kwae | GH111S0087 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Gopdc Kwae | GH111S0087 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Gopdc Kwae | GH111S0087 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hansen Fadama | GH111S0090 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 27 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hansen Fadama | GH111S0090 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hansen Fadama | GH111S0090 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 27 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hansen Fadama | GH111S0090 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 27 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hansen Fadama | GH111S0090 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ho Dome | GH111S0094 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 27 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ho Dome | GH111S0094 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ho Dome | GH111S0094 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ho Dome | GH111S0094 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ho Dome | GH111S0094 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ho Dome | GH111S0094 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ho Dome | GH111S0094 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hohoe | GH111S0095 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 30 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hohoe | GH111S0095 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hohoe | GH111S0095 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hohoe | GH111S0095 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hohoe | GH111S0095 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hohoe | GH111S0095 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hohoe | GH111S0095 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hohoe | GH111S0095 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 27 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 27 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 27 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 27 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kaiser Valley | GH111S0275 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 05 May 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kaiser Valley | GH111S0275 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kaiser Valley | GH111S0275 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 05 May 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kaiser Valley | GH111S0275 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kaiser Valley | GH111S0275 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kaiser Valley | GH111S0275 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kaiser Valley | GH111S0275 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kaiser Valley | GH111S0275 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 16 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 16 Jan 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 06 Aug 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 06 Aug 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 06 Feb 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 28 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 28 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 28 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 28 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 13 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 13 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 13 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 28 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 28 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 28 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 28 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Lawra | GH111S0124 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Lawra | GH111S0124 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 18 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Lawra | GH111S0124 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Lawra | GH111S0124 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 18 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Lawra | GH111S0124 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 18 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Lawra | GH111S0124 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 28 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 28 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 28 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 28 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 11 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 11 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 11 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 11 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 11 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 11 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 11 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | K.15 | Are PV inverters installed in a place that is inaccessible to the public, and protected from rain and UV rays? | Protect and secure the site's photovoltaic installations. | N |  | 11 Mar 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 19 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 19 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 19 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mamfe | GH111S0135 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 27 Apr 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mamfe | GH111S0135 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mamfe | GH111S0135 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 25 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.02d | Is there a maintenance contract dedicated to pressurized installations with submersible pumps ? | Plan to set up a maintenance contract dedicated to pressuried sites equipped with STPs. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.02h | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 automatic gauge on the station. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Install PLLD (Pressurized Line Leak Detector) pressure sensors on all submersible pumps on site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are all the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Is there a forced-running mode for submersible pumps, known and available to station staff? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 25 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 13 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Prévoir l'installation de rails chasse-roues pour sécuriser les fosses dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Prévoir la mise en conformité des installations photovoltaïques pour être conforme à l'invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 13 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 13 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 13 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 21 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 21 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 21 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 26 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 26 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | New Tafo | GH111S0153 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | New Tafo | GH111S0153 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | New Tafo | GH111S0153 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | New Tafo | GH111S0153 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 17 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 17 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 17 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 18 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 18 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 18 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 18 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 08 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 08 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 08 Jan 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 29 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 29 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 29 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 20 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 20 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 20 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 20 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 24 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 24 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 24 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 19 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 19 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 29 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 29 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 29 Dec 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 30 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 30 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 30 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 30 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 30 Jun 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 30 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tema Industrial Area | GH111S0267 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 08 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tema Industrial Area | GH111S0267 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tema Industrial Area | GH111S0267 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tema Industrial Area | GH111S0267 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tema Industrial Area | GH111S0267 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tema Industrial Area | GH111S0267 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tema Industrial Area | GH111S0267 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 09 Oct 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 09 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | H.01 | Is the flooring of the carwash areas non-slippery? | Is the flooring of the carwash areas non-slippery? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 09 Jan 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 16 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 16 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 16 Jul 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 16 Jan 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | G.02 | Are the bay and its storage area clean, with a non-slip floor? | Are the bay and its storage area clean, with a non-slip floor? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Adjust vent distance to make them visible from the offloading and comply with invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 21 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 21 Sep 2025
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Aeroport yaounde | CM111S2211 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Aeroport yaounde | CM111S2211 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation des détecteur de fuite de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Akwa 1 &amp; 2 | CM111S2286 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Akwa 1 &amp; 2 | CM111S2286 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Akwa 1 &amp; 2 | CM111S2286 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Akwa 1 &amp; 2 | CM111S2286 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Awae | CM111S2234 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | Y | Sylvain DJIAGA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Awae | CM111S2234 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | Y | Sylvain DJIAGA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 15 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 15 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 15 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 15 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafia1 | CM111S2207 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | Y | Uriel NGOUBO | 14 Jun 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafia1 | CM111S2207 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Prévoir une remise en état du tableau électrique de la station. | Y | Uriel NGOUBO | 14 Jun 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafia1 | CM111S2207 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Uriel NGOUBO | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafia1 | CM111S2207 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | Y | Uriel NGOUBO | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafia2 | CM111S2216 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafia2 | CM111S2216 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafia2 | CM111S2216 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | Y | Uriel NGOUBO | 17 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafia2 | CM111S2216 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Uriel NGOUBO | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | N |  | 08 Nov 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Prévoir une remise en état du tableau électrique de la station. | N |  | 08 Aug 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Faire réaliser une inspection complète des installations électriques du site par un bureau de contrôle agréé. | N |  | 08 Aug 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Prévoir la mise en place de caniveaux et regards pour récupérer les eaux de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Le personnel de la station est-il informé des règles et obligations liées à la consignation électrique des équipements ? | N |  | 08 Aug 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Prévoir la mise en place de disjoncteurs différentiels 30 mA pour répondre à l'invariants ES07. | N |  | 08 Aug 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Prévoir une rénovation de l'aire de dépotage. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | F.02g | Are all LPG gas cylinders (full and empty) stored more than 3m away from vents and offloading coupling points? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 3m des évents et bouches de dépotage ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 08 Nov 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | G.20 | Is used oil collected and properly treated? | Les huiles usées sont-elles collectées et traitées correctement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 08 Nov 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Sammy EPOUPA | 17 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Une mesure de résistance de la mise à la terre des installations de la station est-elle bien indiquée dans ce rapport ? Et est-elle bien inférieure à 10 ohms ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | F.02f | Are all gas cylinders (full and empty) more than 5m from the site's hydrocarbon tanks or dispensing equipment? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 5m des cuves hydrocarbures ou appareils distributeurs du site ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | Y | Sammy EPOUPA | 17 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bd presidentiel | CM111S2206 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Uriel NGOUBO | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bd presidentiel | CM111S2206 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | Y | Uriel NGOUBO | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bd presidentiel | CM111S2206 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bd presidentiel | CM111S2206 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | Y | Uriel NGOUBO | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bd presidentiel | CM111S2206 | F.02g | Are all LPG gas cylinders (full and empty) stored more than 3m away from vents and offloading coupling points? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 3m des évents et bouches de dépotage ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bd presidentiel | CM111S2206 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bd presidentiel | CM111S2206 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bd presidentiel | CM111S2206 | L.01 | Is the regulatory EV signage present on EV chargers? | La signalétique réglementaire EV est-elle présente sur les bornes de recharge ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Belabo | CM111S2245 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Prévoir la mise en place de pictogrammes "DANGER ÉLECTRIQUE" sur les installations. | N |  | 28 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Belabo | CM111S2245 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Belabo | CM111S2245 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 28 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Belabo | CM111S2245 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Belabo | CM111S2245 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Belabo | CM111S2245 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 28 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Belabo | CM111S2245 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 28 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Belabo | CM111S2245 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bepanda | CM111S2254 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bepanda | CM111S2254 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bepanda | CM111S2254 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bepanda | CM111S2254 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 01 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bepanda yonyong | CM111S2425 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bepanda yonyong | CM111S2425 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bepanda yonyong | CM111S2425 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bepanda yonyong | CM111S2425 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua | CM111S2410 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua | CM111S2410 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua | CM111S2410 | G.02 | Are the bay and its storage area clean, with a non-slip floor? | La baie et sa zone de stockage sont-elles propres avec un sol antidérapant ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua | CM111S2410 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua | CM111S2410 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 10 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua | CM111S2410 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua | CM111S2410 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua | CM111S2410 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 10 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Prévoir l'obturation des fourreaux électriques pour éviter les problème de vapeurs. | N |  | 10 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | E.06 | Are all the offloading coupling ports padlocked? | Les bouches de dépotage sont-elles toutes bien cadenassées ? | N |  | 10 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Les bouches de dépotages sont-elles protégées à l'aide d'un musoir, d'un muret en béton ou de poteaux anti-bélier ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Faire réaliser un raccordement à la terre visible sur les évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 10 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 2 | CM111S2244 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 2 | CM111S2244 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 2 | CM111S2244 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 2 | CM111S2244 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Besseke | CM111S2352 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | Y | Fougere KENGNE | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Besseke | CM111S2352 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Besseke | CM111S2352 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Besseke | CM111S2352 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | Y | Fougere KENGNE | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Besseke | CM111S2352 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Besseke | CM111S2352 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | Y | Fougere KENGNE | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Besseke | CM111S2352 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Fougere KENGNE | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Besseke | CM111S2352 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | Y | Fougere KENGNE | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bessengue | CM111S2350 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Mettre en conformité la distance des évents pour les rendre visibles du dépotage et se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bessengue | CM111S2350 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bessengue | CM111S2350 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bessengue | CM111S2350 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bessengue | CM111S2350 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Biteng | CM111S2405 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Sylvain DJIAGA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonaberi 1 | CM111S2282 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonaberi 1 | CM111S2282 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonaberi 1 | CM111S2282 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonaberi 1 | CM111S2282 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonalembe | CM111S2276 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonalembe | CM111S2276 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonalembe | CM111S2276 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonalembe | CM111S2276 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonalembe | CM111S2276 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonamoudourou | CM111S2260 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonamoudourou | CM111S2260 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonamoudourou | CM111S2260 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonamoudourou | CM111S2260 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonateki 2 | CM111S2275 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonateki 2 | CM111S2275 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonateki 2 | CM111S2275 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonateki 2 | CM111S2275 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonateki 2 | CM111S2275 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonateki 2 | CM111S2275 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonis | CM111S2417 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Jules NYADA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonis | CM111S2417 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Jules NYADA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonis | CM111S2417 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | Y | Jules NYADA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonis | CM111S2417 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | Y | Jules NYADA | 26 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Briqueterie | CM111S2235 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | Y | Sylvain DJIAGA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Briqueterie | CM111S2235 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | Y | Sylvain DJIAGA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Briqueterie | CM111S2235 | G.12 | Is the bay inside lighting sufficient and operational? | Prévoir une remise en état de l'éclairage de la baie. | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Prévoir la mise en place de pictogrammes "DANGER ÉLECTRIQUE" sur les installations. | Y | Sammy EPOUPA | 07 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | N |  | 07 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Prévoir une remise en état du tableau électrique de la station. | N |  | 07 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | Y | Sammy EPOUPA | 07 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Une mesure de résistance de la mise à la terre des installations de la station est-elle bien indiquée dans ce rapport ? Et est-elle bien inférieure à 10 ohms ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Sammy EPOUPA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Prévoir la mise en place du "Réagir en Cas d'Urgence" sur site. | Y | Sammy EPOUPA | 07 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Sammy EPOUPA | 07 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | La date du dernier contrôle des extincteurs est-elle inférieure à 1 an? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | G.12 | Is the bay inside lighting sufficient and operational? | Prévoir une remise en état de l'éclairage de la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 07 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | Y | Sammy EPOUPA | 07 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Ahmat IYABA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | Y | Ahmat IYABA | 10 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Ahmat IYABA | 10 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | Y | Ahmat IYABA | 10 Dec 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dang | CM111S2404 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dang | CM111S2404 | H.02 | Are carwash installations equipped with an emergency stop button? | Les installations de lavage sont-elles équipées d'un bouton d'arrêt d'urgence ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dang | CM111S2404 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dang | CM111S2404 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Ahmat IYABA | 05 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dang | CM111S2404 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Ahmat IYABA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dang | CM111S2404 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dang | CM111S2404 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | Y | Ahmat IYABA | 05 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dang | CM111S2404 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dang | CM111S2404 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dang | CM111S2404 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Djoungolo | CM111S2229 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Djoungolo | CM111S2229 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Djoungolo | CM111S2229 | G.07 | Is the service bay also used for car washing? | La baie de services est-elle également utilisée pour faire du lavage auto ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Djoungolo | CM111S2229 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Djoungolo | CM111S2229 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation des détecteur de fuite de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Djoungolo | CM111S2229 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Djoungolo | CM111S2229 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Y a-t-il des équipements électriques (ex: moteur, pompe) placés à proximité d'une source d'eau ? | N |  | 24 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Prévoir la mise en place d'un extincteur CO2 dédié aux feux d'origine électrique à proximité de chaque coffret électriques du site. | Y | Sammy EPOUPA | 24 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 24 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | Y | Sammy EPOUPA | 24 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | K.09 | Is there a DC breaking device between the inverter and the PV modules? | Prévoir l'installation d'un dispositif de coupure DC sur l'installation PV. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | K.10 | Is there a type 1+2 DC lightning and surge arrester on the PV system? | Y a-t-il bien un dispositif parafoudre DC de type 1+2 sur l'installation PV ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | K.11 | Is there a 300mA differential circuit breaker upstream of the PV system? | Prévoir l'installation d'un disjoncteur différentiel 300mA pour l'installation PV. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Prévoir la mise en conformité de la signalétique des installations photovoltaïques du site. | N |  | 24 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Prévoir la mise en conformité des installations photovoltaïques pour être conforme à l'invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 24 Jan 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | K.12 | Is there a Type 2 surge protection device in the PV system's AC cabinet? | Installer un dispositif de protection contre les surtensions Type 2 dans le coffret AC de l'installation PV. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | Dans le cadre de la solarisation de la station, une étude de structure a-t-elle bien été réalisée pour chaque structure recevant des modules PV ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | K.07 | Do photovoltaic systems have a dedicated emergency stop button? | Prévoir la mise en place d'un arrêt d'urgence dédiés au solaire. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Dschang 2 | CM111S2354 | K.15 | Are PV inverters installed in a place that is inaccessible to the public, and protected from rain and UV rays? | Prévoir la protection et la sécurisation des installations photovoltaïque du site. | N |  | 24 Apr 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ebom | CM111S4223 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ebom | CM111S4223 | G.12 | Is the bay inside lighting sufficient and operational? | Prévoir une remise en état de l'éclairage de la baie. | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ekoumdoum | CM111S2358 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Sylvain DJIAGA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Essos | CM111S2241 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Sylvain DJIAGA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Essos | CM111S2241 | G.12 | Is the bay inside lighting sufficient and operational? | Prévoir une remise en état de l'éclairage de la baie. | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Essos | CM111S2241 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Essos | CM111S2241 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | Y | Sylvain DJIAGA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Essos | CM111S2241 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | Y | Sylvain DJIAGA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Essos | CM111S2241 | G.16 | Are the fire extinguishers in the bay sealed? | Les extincteurs de la baie sont-ils plombés ? | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Essos | CM111S2241 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | La date du dernier contrôle des extincteurs est-elle inférieure à 1 an? | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Etoudi | CM111S2212 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Etrier | CM111S2221 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | Y | Sylvain DJIAGA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Etrier | CM111S2221 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Etrier | CM111S2221 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Etrier | CM111S2221 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation des détecteur de fuite de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Etrier | CM111S2221 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Etrier | CM111S2221 | G.12 | Is the bay inside lighting sufficient and operational? | Prévoir une remise en état de l'éclairage de la baie. | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Figuil | CM111S2302 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Ahmat IYABA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Figuil | CM111S2302 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Figuil | CM111S2302 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Figuil | CM111S2302 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Prévoir la mise en conformité de la signalétique des installations photovoltaïques du site. | Y | Ahmat IYABA | 06 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Figuil | CM111S2302 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Figuil | CM111S2302 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Figuil | CM111S2302 | F.02f | Are all gas cylinders (full and empty) more than 5m from the site's hydrocarbon tanks or dispensing equipment? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 5m des cuves hydrocarbures ou appareils distributeurs du site ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Figuil | CM111S2302 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | Y | Ahmat IYABA | 06 Dec 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Figuil | CM111S2302 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Figuil | CM111S2302 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Figuil | CM111S2302 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Goshen olympic | CM111S5209 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | Y | Sylvain DJIAGA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Goshen olympic | CM111S5209 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | Y | Sylvain DJIAGA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Guider | CM111S2305 | F.02g | Are all LPG gas cylinders (full and empty) stored more than 3m away from vents and offloading coupling points? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 3m des évents et bouches de dépotage ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Guider | CM111S2305 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Ahmat IYABA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Guider | CM111S2305 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Guider | CM111S2305 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Laquintinie | CM111S2278 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Laquintinie | CM111S2278 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Laquintinie | CM111S2278 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Magzi yaounde | CM111S2355 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Magzi yaounde | CM111S2355 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Magzi yaounde | CM111S2355 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | Y | Sylvain DJIAGA | 15 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Magzi yaounde | CM111S2355 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Magzi yaounde | CM111S2355 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mandjou bertoua | CM111S2408 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Jules NYADA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mandjou bertoua | CM111S2408 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Jules NYADA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mandjou bertoua | CM111S2408 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | Y | Jules NYADA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mandjou bertoua | CM111S2408 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | Y | Jules NYADA | 26 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Maroua 1 | CM111S2298 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Ahmat IYABA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Maroua 1 | CM111S2298 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Maroua 1 | CM111S2298 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | Y | Ahmat IYABA | 25 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Maroua 1 | CM111S2298 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Maroua 1 | CM111S2298 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Maroua 1 | CM111S2298 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Maroua 1 | CM111S2298 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Ahmat IYABA | 25 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Maroua 2 | CM111S2304 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Ahmat IYABA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Maroua 2 | CM111S2304 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Maroua 2 | CM111S2304 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Y a-t-il des équipements électriques (ex: moteur, pompe) placés à proximité d'une source d'eau ? | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Les bouches de dépotages sont-elles protégées à l'aide d'un musoir, d'un muret en béton ou de poteaux anti-bélier ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | L'aire de dépotage est-elle équipée d'un système de raccordement à la terre pour connecter le camion de livraison : piquet / pince / enrouleur ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | C.02 | Is the following signage present on forecourt islands: Use of cell phone forbidden? | Prévoir la mise en place de pictogrammes "Téléphones Interdits" sur la piste. | Y | Sammy EPOUPA | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | C.03 | Is the following signage present on forecourt islands: Engine shutdown required? | Prévoir la mise en place de pictogrammes "Arrêt du Moteur" sur la piste. | Y | Sammy EPOUPA | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | La base des appareils distributeurs est-elle propre, sans fuite de carburant apparente sur les îlots de distribution ? | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | Y | Sammy EPOUPA | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | C.01 | Is the following signage present on forecourt islands: No smoking? | Prévoir la mise en place de pictogrammes "Défense de fumer" sur la piste. | Y | Sammy EPOUPA | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Sammy EPOUPA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Mettre en conformité la distance des évents pour les rendre visibles du dépotage et se conformer à l'invariant EP09. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Faire réaliser un raccordement à la terre visible sur les évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Sammy EPOUPA | 14 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 14 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 1 | CM111S2325 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | L'ensemble des équipements de la baie peut-il être neutralisé par un bouton d'arrêt d'urgence ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | C.11a | Is there a shovel in every sandbox? | Y a-t-il bien une pelle dans chaque bac à sable ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | N |  | 24 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Prévoir une remise en état du tableau électrique de la station. | Y | Sammy EPOUPA | 24 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | Y | Sammy EPOUPA | 24 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Sammy EPOUPA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 24 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Sammy EPOUPA | 24 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | Y | Sammy EPOUPA | 24 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mbouda 2 | CM111S2332 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Meiganga | CM111S2301 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Meiganga | CM111S2301 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Meiganga | CM111S2301 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Meiganga | CM111S2301 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | Y | Ahmat IYABA | 06 Dec 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Meiganga | CM111S2301 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Meiganga | CM111S2301 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Meiganga | CM111S2301 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melen 2 | CM111S2238 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 12 Nov 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melen 2 | CM111S2238 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melen 2 | CM111S2238 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 12 Nov 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melen 2 | CM111S2238 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Prévoir une remise en conformité des dépotages selon l'Invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melen 2 | CM111S2238 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Prévoir une remise en conformité des dépotages selon l'Invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Une mesure de résistance de la mise à la terre des installations de la station est-elle bien indiquée dans ce rapport ? Et est-elle bien inférieure à 10 ohms ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | E.06 | Are all the offloading coupling ports padlocked? | Les bouches de dépotage sont-elles toutes bien cadenassées ? | Y | Sammy EPOUPA | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Sammy EPOUPA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Sammy EPOUPA | 14 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Toutes les bouteilles de gaz (pleines et vides) sont-elles rangées sur des racks ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | Y | Sammy EPOUPA | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 14 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Melong | CM111S2327 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Messa 2 | CM111S2226 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Prévoir une remise en état des caniveaux de la piste de distribution. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Messa 2 | CM111S2226 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Messa 2 | CM111S2226 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation de détecteurs de fuites de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Messa 2 | CM111S2226 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 12 Nov 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Messa 2 | CM111S2226 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipements de baie. | N |  | 12 Nov 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 1 | CM111S2217 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 07 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 1 | CM111S2217 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 1 | CM111S2217 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 1 | CM111S2217 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Uriel NGOUBO | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | G.12 | Is the bay inside lighting sufficient and operational? | Prévoir une remise en état de l'éclairage de la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | Y | Uriel NGOUBO | 10 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Prévoir la mise en place de têtes de jauge type "baïonnette" sur site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Uriel NGOUBO | 10 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Mfoundassi 2 | CM111S2222 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Monatele | CM111S2201 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | Y | Uriel NGOUBO | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Monatele | CM111S2201 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | Y | Uriel NGOUBO | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Monatele | CM111S2201 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Uriel NGOUBO | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Monatele | CM111S2201 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | N'dere depot | CM111S2309 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | N'dere depot | CM111S2309 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | Y | Ahmat IYABA | 05 Dec 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | N'dere depot | CM111S2309 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | N'dere depot | CM111S2309 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | N'dere depot | CM111S2309 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | N'dere depot | CM111S2309 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Prévoir la mise en place d'un système de traitement des eaux usées selon l'invariant ET03. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Ahmat IYABA | 06 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | Y | Ahmat IYABA | 06 Dec 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | Y | Ahmat IYABA | 06 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ngaoundal | CM111S2296 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkolbisson | CM111S2308 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation de détecteurs de fuites de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkolnda | CM111S1702 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkolndongo | CM111S2219 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkolndongo | CM111S2219 | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkolndongo | CM111S2219 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Prévoir la mise en place de têtes de jauge type "baïonnette" sur site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkolndongo | CM111S2219 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkolndongo | CM111S2219 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 21 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkolndongo | CM111S2219 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs disposent-ils de systèmes de vérifications périodiques de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkolndongo | CM111S2219 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 21 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 1 | CM111S2213 | G.07 | Is the service bay also used for car washing? | La baie de services est-elle également utilisée pour faire du lavage auto ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 1 | CM111S2213 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 1 | CM111S2213 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Les portiques et autres équipements mobiles de lavage sont-ils tous correctement positionnés pour éviter tout risque d'écrasement en fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 1 | CM111S2213 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 1 | CM111S2213 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 2 | CM111S2240 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 2 | CM111S2240 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 2 | CM111S2240 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 2 | CM111S2240 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 10 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 2 | CM111S2240 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 10 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 2 | CM111S2240 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomkana 2 | CM111S2240 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomo | CM111S3202 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | Y | Sylvain DJIAGA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomo | CM111S3202 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Sylvain DJIAGA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomo | CM111S3202 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Sylvain DJIAGA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nkomo | CM111S3202 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nsazomo | CM111S1701 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | Y | Sylvain DJIAGA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nsimeyong | CM111S2403 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Sylvain DJIAGA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Nsimeyong | CM111S2403 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Sylvain DJIAGA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | Y | Uriel NGOUBO | 13 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Prévoir l'obturation des fourreaux électriques pour éviter les problème de vapeurs. | Y | Uriel NGOUBO | 13 Jun 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | Y | Uriel NGOUBO | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | Y | Uriel NGOUBO | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | G.12 | Is the bay inside lighting sufficient and operational? | Prévoir une remise en état de l'éclairage de la baie. | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | Y | Uriel NGOUBO | 13 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Uriel NGOUBO | 13 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | Y | Uriel NGOUBO | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Obala | CM111S2225 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | Y | Uriel NGOUBO | 13 Dec 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Odza | CM111S2418 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Odza | CM111S2418 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Okolo | CM111S2214 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Uriel NGOUBO | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Okolo | CM111S2214 | G.12 | Is the bay inside lighting sufficient and operational? | Prévoir une remise en état de l'éclairage de la baie. | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Okolo | CM111S2214 | F.02g | Are all LPG gas cylinders (full and empty) stored more than 3m away from vents and offloading coupling points? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 3m des évents et bouches de dépotage ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Okolo | CM111S2214 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | Y | Uriel NGOUBO | 13 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Okolo | CM111S2214 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Okolo | CM111S2214 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Okolo | CM111S2214 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | Y | Uriel NGOUBO | 13 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Okolo | CM111S2214 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Okolo | CM111S2214 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Okolo | CM111S2214 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | Y | Uriel NGOUBO | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | President | CM111S2262 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | R.p.nlongkak | CM111S2228 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | Y | Sylvain DJIAGA | 09 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | R.p.nlongkak | CM111S2228 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Prévoir une remise en état du tableau électrique de la station. | Y | Sylvain DJIAGA | 09 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | R.p.nlongkak | CM111S2228 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Y a-t-il des équipements électriques (ex: moteur, pompe) placés à proximité d'une source d'eau ? | Y | Sylvain DJIAGA | 09 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Reunification | CM111S2348 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Reunification | CM111S2348 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Reunification | CM111S2348 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Reunification | CM111S2348 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | Y | Fougere KENGNE | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Route garoua | CM111S2299 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | Y | Ahmat IYABA | 10 Jun 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Route garoua | CM111S2299 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Route garoua | CM111S2299 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Ahmat IYABA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Route garoua | CM111S2299 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Route garoua | CM111S2299 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Route garoua | CM111S2299 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Route garoua | CM111S2299 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | Y | Ahmat IYABA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Route garoua | CM111S2299 | F.02g | Are all LPG gas cylinders (full and empty) stored more than 3m away from vents and offloading coupling points? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 3m des évents et bouches de dépotage ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Route garoua | CM111S2299 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Route garoua | CM111S2299 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | Y | Ahmat IYABA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Rue manguier | CM111S2401 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Rue manguier | CM111S2401 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 19 Nov 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Rue manguier | CM111S2401 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipements de baie. | N |  | 19 Nov 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sa'a | CM111S4101 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 28 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Prévoir l'obturation des fourreaux électriques pour éviter les problème de vapeurs. | N |  | 28 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 28 Jul 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | H.02 | Are carwash installations equipped with an emergency stop button? | Les installations de lavage sont-elles équipées d'un bouton d'arrêt d'urgence ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 28 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Sifa nkongsamba | CM111S2338 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Tsinga | CM111S2202 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Tsinga | CM111S2202 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 19 Nov 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Tsinga | CM111S2202 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipements de baie. | N |  | 19 Nov 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Tsinga | CM111S2202 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Prévoir une remise en conformité des dépotages selon l'Invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Tsinga | CM111S2202 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Prévoir une remise en conformité des dépotages selon l'Invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | Y | Sammy EPOUPA | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | Y | Sammy EPOUPA | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Une mesure de résistance de la mise à la terre des installations de la station est-elle bien indiquée dans ce rapport ? Et est-elle bien inférieure à 10 ohms ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | E.11a | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | Si "NON", un périmètre de sécurité de 5m autours du dépotage doit être mis en place, avec neutralisation temporaire des îlots adjacents. Le personnel du site est-il au courant ? | Y | Sammy EPOUPA | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | Y | Sammy EPOUPA | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Prévoir le raccordement des réservoirs du site au réseau de mise à la terre. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | Y | Sammy EPOUPA | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | Y | Sammy EPOUPA | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 12 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | Y | Sammy EPOUPA | 12 Sep 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | Y | Sammy EPOUPA | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | Y | Sammy EPOUPA | 12 Dec 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Unite | CM111S2312 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Wouri 1 | CM111S2277 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Wouri 1 | CM111S2277 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Wouri 1 | CM111S2277 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Wouri 1 | CM111S2277 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Wouri 2 | CM111S2351 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Wouri 2 | CM111S2351 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Wouri 2 | CM111S2351 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 26 Oct 2025
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Wouri 2 | CM111S2351 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Wouri 2 | CM111S2351 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Les bouches de dépotages sont-elles protégées à l'aide d'un musoir, d'un muret en béton ou de poteaux anti-bélier ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Les bouches de dépotage sont-elles visiblement reliés au réseau de terre de la station à l'aide d'un câble en cuivre de 16 mm2 de section minimum? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs disposent-ils de systèmes de vérifications périodiques de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | 8 Tranche | CI111S2361 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 06 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | D.26 | Are vent heads at least 4m high from the ground? | Rehausser les têtes d'évents pour être conforme à l'invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 06 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | G.02 | Are the bay and its storage area clean, with a non-slip floor? | La baie et sa zone de stockage sont-elles propres avec un sol antidérapant ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Mettre en conformité la distance des évents pour les rendre visibles du dépotage et se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | H.01 | Is the flooring of the carwash areas non-slippery? | Le revêtement de sol des aires de lavage est-il antidérapant ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 1 | CI111S2201 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 06 Feb 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 2 | CI111S2205 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 06 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 2 | CI111S2205 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 2 | CI111S2205 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 2 | CI111S2205 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 2 | CI111S2205 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 2 | CI111S2205 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 2 | CI111S2205 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 2 | CI111S2205 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 2 | CI111S2205 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou 2 | CI111S2205 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 06 Feb 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou Gr | CI111S2218 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou Gr | CI111S2218 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou Gr | CI111S2218 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou Gr | CI111S2218 | G.20 | Is used oil collected and properly treated? | Les huiles usées sont-elles collectées et traitées correctement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou Gr | CI111S2218 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou Gr | CI111S2218 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou Gr | CI111S2218 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abengourou Gr | CI111S2218 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Prévoir une rénovation de l'aire de dépotage. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Les bouches de dépotages sont-elles protégées à l'aide d'un musoir, d'un muret en béton ou de poteaux anti-bélier ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs disposent-ils de systèmes de vérifications périodiques de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobo Azur | CI111S2443 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 05 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 05 Feb 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Abobodoume | CI111S2402 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Adzopé 1 | CI111S2210 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 06 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Adzopé 1 | CI111S2210 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Adzopé 1 | CI111S2210 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Adzopé 1 | CI111S2210 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Adzopé 1 | CI111S2210 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Adzopé 1 | CI111S2210 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Adzopé 1 | CI111S2210 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 06 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Adzopé 1 | CI111S2210 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Adzopé 1 | CI111S2210 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Adzopé 1 | CI111S2210 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Adzopé 1 | CI111S2210 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 06 Feb 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 07 Feb 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Gr2 | CI111S2232 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Agboville Rail | CI111S2231 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Akoupé | CI111S2236 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 06 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Akoupé | CI111S2236 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Akoupé | CI111S2236 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Akoupé | CI111S2236 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Akoupé | CI111S2236 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Akoupé | CI111S2236 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 06 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Akoupé | CI111S2236 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Akoupé | CI111S2236 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Akoupé | CI111S2236 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 06 Feb 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Avenue de Marcory | CI111S2429 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Avenue de Marcory | CI111S2429 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Avenue de Marcory | CI111S2429 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Avenue de Marcory | CI111S2429 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Avenue de Marcory | CI111S2429 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Avenue de Marcory | CI111S2429 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Avenue de Marcory | CI111S2429 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Avenue de Marcory | CI111S2429 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Avenue de Marcory | CI111S2429 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Avenue de Marcory | CI111S2429 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | B.16 | Does the station have a general emergency stop button ? | Prévoir l'installation d'un coup de poing d'arrêt d'urgence général pour le site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Prévoir la mise en place d'un séparateur hydrocarbures piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 30 Sep 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | K.07 | Do photovoltaic systems have a dedicated emergency stop button? | Prévoir la mise en place d'un arrêt d'urgence dédiés au solaire. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Hôpital | CI111S2220 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Bonoua Mosquée | CI111S2277 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Cite Sir | CI111S2465 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Cite Sir | CI111S2465 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Cite Sir | CI111S2465 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Cite Sir | CI111S2465 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Cite Sir | CI111S2465 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Cite Sir | CI111S2465 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Cite Sir | CI111S2465 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Cite Sir | CI111S2465 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Cite Sir | CI111S2465 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Cite Sir | CI111S2465 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Cite Sir | CI111S2465 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Prévoir la mise en place de caniveaux et regards pour récupérer les eaux de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | C.10 | Is the offloading area connected to an oil separator? | Prévoir la mise en place d'un séparateur ou le raccordement de la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Prévoir une rénovation de l'aire de dépotage. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | L'aire de dépotage est-elle équipée d'un système de raccordement à la terre pour connecter le camion de livraison : piquet / pince / enrouleur ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Prévoir la mise en place d'un séparateur hydrocarbures piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 1 | CI111S2204 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | B.16 | Does the station have a general emergency stop button ? | Prévoir l'installation d'un coup de poing d'arrêt d'urgence général pour le site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Prévoir la mise en place de caniveaux et regards pour récupérer les eaux de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | C.10 | Is the offloading area connected to an oil separator? | Prévoir la mise en place d'un séparateur ou le raccordement de la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Prévoir la mise en place d'un séparateur hydrocarbures piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Dabou 2 | CI111S2207 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | B.16 | Does the station have a general emergency stop button ? | Prévoir l'installation d'un coup de poing d'arrêt d'urgence général pour le site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Prévoir une rénovation de l'aire de dépotage. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Daoukro | CI111S2255 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Prévoir une rénovation de l'aire de dépotage. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Les bouches de dépotages sont-elles protégées à l'aide d'un musoir, d'un muret en béton ou de poteaux anti-bélier ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Marché | CI111S2272 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | B.16 | Does the station have a general emergency stop button ? | Prévoir l'installation d'un coup de poing d'arrêt d'urgence général pour le site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Divo Relais | CI111S2283 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Grand Bereby | CI111S2430 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Kmssi Pango-Ne | CI111S2310 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Marcory Resid | CI111S2285 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Marcory Resid | CI111S2285 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Marcory Resid | CI111S2285 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Marcory Resid | CI111S2285 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Marcory Resid | CI111S2285 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Marcory Resid | CI111S2285 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Marcory Resid | CI111S2285 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Marcory Resid | CI111S2285 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Marcory Resid | CI111S2285 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Marcory Resid | CI111S2285 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Martyrs | CI111S2273 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Martyrs | CI111S2273 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Martyrs | CI111S2273 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Martyrs | CI111S2273 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Martyrs | CI111S2273 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Martyrs | CI111S2273 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Martyrs | CI111S2273 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Martyrs | CI111S2273 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Martyrs | CI111S2273 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Martyrs | CI111S2273 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Minignan | CI111S2433 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Minignan | CI111S2433 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Minignan | CI111S2433 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Minignan | CI111S2433 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Minignan | CI111S2433 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Minignan | CI111S2433 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | La base des appareils distributeurs est-elle propre, sans fuite de carburant apparente sur les îlots de distribution ? | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Les portiques et autres équipements mobiles de lavage sont-ils tous correctement positionnés pour éviter tout risque d'écrasement en fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | N'douci Gr | CI111S2312 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | La base des appareils distributeurs est-elle propre, sans fuite de carburant apparente sur les îlots de distribution ? | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Odienné | CI111S2331 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Palais Justice | CI111S2408 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur tous les compartiments de carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Palais Justice | CI111S2408 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Palais Justice | CI111S2408 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve acoustique des installations pétrolières du site. | N |  | 12 May 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Palais Justice | CI111S2408 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe et être conforme à l'EP06 | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Palais Justice | CI111S2408 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 12 Nov 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Palais Justice | CI111S2408 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Palais Justice | CI111S2408 | D.06 | Are all the station's fuel tanks double-walled? | Prévoir le remplacement des réservoirs simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Riviéra Bonoum | CI111S2251 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Route Anyama | CI111S2427 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Prévoir une remise en état du tableau électrique de la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Prévoir l'obturation des fourreaux électriques pour éviter les problème de vapeurs. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Prévoir la mise en conformité des installations photovoltaïques pour être conforme à l'invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | S Pedro Bardot | CI111S2307 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Les portiques et autres équipements mobiles de lavage sont-ils tous correctement positionnés pour éviter tout risque d'écrasement en fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | San Pedro Zi | CI111S2229 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | C.02 | Is the following signage present on forecourt islands: Use of cell phone forbidden? | Plan to install “Cell Phones Forbidden” pictograms on the forecourt. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | C.03 | Is the following signage present on forecourt islands: Engine shutdown required? | Plan to install “Engine Stop” pictograms on the forecourt. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sassandra | CI111S2293 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Sikensi | CI111S2295 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Prévoir la remise en état de la signalétique du tableau électrique de la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Prévoir la mise en place de pictogrammes "DANGER ÉLECTRIQUE" sur les installations. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Prévoir une remise en état du tableau électrique de la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou | CI111S2301 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Tabou 2 | CI111S2444 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Prévoir la remise en état de la signalétique du tableau électrique de la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | Si la baie est équipée de fosses, sont-elles toutes sécurisées à l'aide d'un caillebotis galvanisés ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Prévoir la mise en conformité des installations photovoltaïques pour être conforme à l'invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 30 Jun 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Touba | CI111S2329 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 31 Mar 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Prévoir l'installation de rails chasse-roues pour sécuriser les fosses dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 30 Sep 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Vridi A | CI111S2233 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Autor Nord | CI111S2241 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Autor Nord | CI111S2241 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Autor Nord | CI111S2241 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Autor Nord | CI111S2241 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Autor Nord | CI111S2241 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Autor Nord | CI111S2241 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Autor Nord | CI111S2241 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Autor Nord | CI111S2241 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 05 Feb 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Autor Nord | CI111S2241 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Autor Nord | CI111S2241 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 13 Nov 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe et être conforme à l'EP06 | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 13 Nov 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotages pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure selon l'Invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 13 Nov 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Banco Sud | CI111S2246 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Prévoir une remise en conformité du traitement des eaux de la baie selon l'Invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Bel Air | CI111S2247 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 05 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Bel Air | CI111S2247 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Bel Air | CI111S2247 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Bel Air | CI111S2247 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Bel Air | CI111S2247 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Bel Air | CI111S2247 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Bel Air | CI111S2247 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Bel Air | CI111S2247 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Bel Air | CI111S2247 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Bel Air | CI111S2247 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Figayo | CI111S2240 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Figayo | CI111S2240 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 13 Nov 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Figayo | CI111S2240 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Figayo | CI111S2240 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Figayo | CI111S2240 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve acoustique des installations pétrolières du site. | N |  | 13 May 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Figayo | CI111S2240 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe et être conforme à l'EP06 | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Figayo | CI111S2240 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 13 Nov 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Figayo | CI111S2240 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Figayo | CI111S2240 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotages pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Figayo | CI111S2240 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure selon l'Invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Figayo | CI111S2240 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Selmer | CI111S2294 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 12 Nov 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Selmer | CI111S2294 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Selmer | CI111S2294 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve acoustique des installations pétrolières du site. | N |  | 12 May 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Selmer | CI111S2294 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe et être conforme à l'EP06 | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Selmer | CI111S2294 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 12 Nov 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Selmer | CI111S2294 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Selmer | CI111S2294 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotages pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Selmer | CI111S2294 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yop Selmer | CI111S2294 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Prévoir une remise en conformité du traitement des eaux de la baie selon l'Invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yopougon Sideci | CI111S2428 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 05 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yopougon Sideci | CI111S2428 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 05 Aug 2025
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yopougon Sideci | CI111S2428 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yopougon Sideci | CI111S2428 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yopougon Sideci | CI111S2428 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yopougon Sideci | CI111S2428 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yopougon Sideci | CI111S2428 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yopougon Sideci | CI111S2428 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yopougon Sideci | CI111S2428 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Côte d'Ivoire | Yopougon Sideci | CI111S2428 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 16 Jul 2025
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 16 Jul 2025
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | D.28 | Are the vents more than 3 meters from an electrical source? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | L'ensemble des équipements de la baie peut-il être neutralisé par un bouton d'arrêt d'urgence ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 16 Oct 2025
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 16 Oct 2025
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Aéroport | GA111S0012 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 22 Jul 2025
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Les portiques et autres équipements mobiles de lavage sont-ils tous correctement positionnés pour éviter tout risque d'écrasement en fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 22 Oct 2025
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 22 Jul 2025
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | L'ensemble des équipements de la baie peut-il être neutralisé par un bouton d'arrêt d'urgence ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | H.02 | Are carwash installations equipped with an emergency stop button? | Les installations de lavage sont-elles équipées d'un bouton d'arrêt d'urgence ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 22 Oct 2025
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs disposent-ils de systèmes de vérifications périodiques de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Gabon | Pont-M'pirah | GA111S0020 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 22 Jan 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Alep | GQ111S0030 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Alep | GQ111S0030 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Alep | GQ111S0030 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 28 Sep 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Alep | GQ111S0030 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Alep | GQ111S0030 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Alep | GQ111S0030 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Alep | GQ111S0030 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Les employés de la station sont-il bien équipés des EPI réglementaires : gilet fluo + casque + chaussure de sécurité + gants + lunettes ? | N |  | 28 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 12 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 12 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 12 Oct 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 12 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 12 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 12 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Anisok | GQ111S0009 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Banapa | GQ111S0027 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Banapa | GQ111S0027 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Banapa | GQ111S0027 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Banapa | GQ111S0027 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Banapa | GQ111S0027 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Banapa | GQ111S0027 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Banapa | GQ111S0027 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Banapa | GQ111S0027 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 14 Oct 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Banapa | GQ111S0027 | K.15 | Are PV inverters installed in a place that is inaccessible to the public, and protected from rain and UV rays? | Protect and secure the site's photovoltaic installations. | N |  | 14 Apr 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Banapa | GQ111S0027 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 02 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | N |  | 02 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 02 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 02 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | C.11c | Is the sand clean and free of waste in all sandboxes | Is the sand clean and free of waste in all sandboxes | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 02 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 02 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ebibeyin | GQ111S0010 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ekuku | GQ111S0003 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ekuku | GQ111S0003 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ekuku | GQ111S0003 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ekuku | GQ111S0003 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 20 Sep 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ekuku | GQ111S0003 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ekuku | GQ111S0003 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 20 Dec 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ekuku | GQ111S0003 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ekuku | GQ111S0003 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ekuku | GQ111S0003 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ekuku | GQ111S0003 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 20 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Evinayong | GQ111S0011 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 16 Nov 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Evinayong | GQ111S0011 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Evinayong | GQ111S0011 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 16 May 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Evinayong | GQ111S0011 | J.07 | Is the station connected to the public wastewater network (sewers)? | Ensure that the site's wastewater complies with Invariant ET03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Prévoir la remise en état de la signalétique du tableau électrique de la station. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Le personnel de la station est-il informé des règles et obligations liées à la consignation électrique des équipements ? | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Les bouches de dépotage sont-elles visiblement reliés au réseau de terre de la station à l'aide d'un câble en cuivre de 16 mm2 de section minimum? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Prévoir une remise en état des caniveaux de la piste de distribution. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | C.11c | Is the sand clean and free of waste in all sandboxes | Le sable est-il propre et exempt de déchets dans tous les bacs ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Prévoir la mise en place de têtes de jauge type "baïonnette" sur site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | D.16 | Does the station have a graduated gauge ruler in good condition, allowing manual gauging to be carried out? | Fournir une règle de jauge à la station. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Faire réaliser un raccordement à la terre visible sur les évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 14 Oct 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs disposent-ils de systèmes de vérifications périodiques de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Kogo | GQ111S0006 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 26 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 26 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 26 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 26 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 26 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 26 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | K.07 | Do photovoltaic systems have a dedicated emergency stop button? | Plan to install a dedicated solar emergency stop. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Libertad | GQ111S0002 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 26 Dec 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Los Ángeles | GQ111S0024 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Los Ángeles | GQ111S0024 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 12 Nov 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | N |  | 14 Oct 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Prévoir la mise en place de têtes de jauge type "baïonnette" sur site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 14 Oct 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs disposent-ils de systèmes de vérifications périodiques de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Les employés de la station sont-il bien équipés des EPI réglementaires : gilet fluo + casque + chaussure de sécurité + gants + lunettes ? | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbini | GQ111S0012 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 14 Jan 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 06 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 06 Nov 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mbogo Nsogo | GQ111S0004 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 02 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 02 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 02 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 02 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 02 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 02 Nov 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Micomiseng | GQ111S0013 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 01 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 01 Oct 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 01 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 01 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 01 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 01 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | N |  | 01 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 01 Oct 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Mongomo | GQ111S0014 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ngolo | GQ111S0005 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 28 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ngolo | GQ111S0005 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Plan to restore the gutters on the forecourt area. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ngolo | GQ111S0005 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ngolo | GQ111S0005 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ngolo | GQ111S0005 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ngolo | GQ111S0005 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ngolo | GQ111S0005 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ngolo | GQ111S0005 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ngolo | GQ111S0005 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 28 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ngolo | GQ111S0005 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Niefang | GQ111S0015 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 06 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Niefang | GQ111S0015 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Niefang | GQ111S0015 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Niefang | GQ111S0015 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Niefang | GQ111S0015 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Niefang | GQ111S0015 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Niefang | GQ111S0015 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Niefang | GQ111S0015 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Niefang | GQ111S0015 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Niefang | GQ111S0015 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 06 Nov 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Niefang | GQ111S0015 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | C.02 | Is the following signage present on forecourt islands: Use of cell phone forbidden? | Plan to install “Cell Phones Forbidden” pictograms on the forecourt. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | C.03 | Is the following signage present on forecourt islands: Engine shutdown required? | Plan to install “Engine Stop” pictograms on the forecourt. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | C.01 | Is the following signage present on forecourt islands: No smoking? | Plan to install “No smoking” pictograms on the forecourt. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 14 Oct 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 14 Jul 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Nsok Nsomo | GQ111S0017 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 14 Jan 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ntobo | GQ111S0033 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 13 Nov 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ntobo | GQ111S0033 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ntobo | GQ111S0033 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ntobo | GQ111S0033 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ntobo | GQ111S0033 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Ntobo | GQ111S0033 | J.07 | Is the station connected to the public wastewater network (sewers)? | Ensure that the site's wastewater complies with Invariant ET03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | D.04 | Are all the station's fuel tanks underground? | Plan the eradication of above-ground tanks on site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | D.09 | Are manual gauging/dipping heads easily accessible to the station staff (maximum 30 cm below forecourt road cover)? | Are manual gauging/dipping heads easily accessible to the station staff (maximum 30 cm below forecourt road cover)? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 07 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 07 Nov 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Oyala | GQ111S0031 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 07 Feb 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Paseo Marítimo | GQ111S0023 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Paseo Marítimo | GQ111S0023 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Paseo Marítimo | GQ111S0023 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Paseo Marítimo | GQ111S0023 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Paseo Marítimo | GQ111S0023 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Paseo Marítimo | GQ111S0023 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Paseo Marítimo | GQ111S0023 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 31 Dec 2025
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Paseo Marítimo | GQ111S0023 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Tres de Agosto Malabo | GQ111S0018 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Tres de Agosto Malabo | GQ111S0018 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Tres de Agosto Malabo | GQ111S0018 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Tres de Agosto Malabo | GQ111S0018 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Tres de Agosto Malabo | GQ111S0018 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinea Ecuatorial | Tres de Agosto Malabo | GQ111S0018 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Prévoir la mise en place de pictogrammes "DANGER ÉLECTRIQUE" sur les installations. | N |  | 16 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 16 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | C.01 | Is the following signage present on forecourt islands: No smoking? | Prévoir la mise en place de pictogrammes "Défense de fumer" sur la piste. | N |  | 16 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | C.03 | Is the following signage present on forecourt islands: Engine shutdown required? | Prévoir la mise en place de pictogrammes "Arrêt du Moteur" sur la piste. | N |  | 16 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Prévoir la mise en place de têtes de jauge type "baïonnette" sur site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 16 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 16 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | C.02 | Is the following signage present on forecourt islands: Use of cell phone forbidden? | Prévoir la mise en place de pictogrammes "Téléphones Interdits" sur la piste. | N |  | 16 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | C.15a | If "YES", is the site equipped with an emergency call system connected to a remote monitoring center or to a person designated and trained to handle incidents? | Prévoir la mis en conformité de l'invariant ES08 sur les distributions sans surveillance. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Prévoir le raccordement des réservoirs du site au réseau de mise à la terre. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | La date du dernier contrôle des extincteurs est-elle inférieure à 1 an? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | G.16 | Are the fire extinguishers in the bay sealed? | Les extincteurs de la baie sont-ils plombés ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa bollondé | GN111S0480 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 16 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Prévoir la mise en place d'un extincteur CO2 dédié aux feux d'origine électrique à proximité de chaque coffret électriques du site. | N |  | 17 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | C.02 | Is the following signage present on forecourt islands: Use of cell phone forbidden? | Prévoir la mise en place de pictogrammes "Téléphones Interdits" sur la piste. | N |  | 17 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Prévoir une remise en état des caniveaux de la piste de distribution. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | C.12 | Is the forecourt equipped with one ABC powder extinguisher per island? | Prévoir la mise en place d'un extincteur ABC par îlot de distribution. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | C.15a | If "YES", is the site equipped with an emergency call system connected to a remote monitoring center or to a person designated and trained to handle incidents? | Prévoir la mis en conformité de l'invariant ES08 sur les distributions sans surveillance. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Prévoir la mise en place de pictogrammes "DANGER ÉLECTRIQUE" sur les installations. | N |  | 17 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | C.01 | Is the following signage present on forecourt islands: No smoking? | Prévoir la mise en place de pictogrammes "Défense de fumer" sur la piste. | N |  | 17 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | C.03 | Is the following signage present on forecourt islands: Engine shutdown required? | Prévoir la mise en place de pictogrammes "Arrêt du Moteur" sur la piste. | N |  | 17 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | C.11 | Does the station have a sandbox per forecourt area? | Prévoir la mise en place de bacs à sable pour répondre à l'invariant ES01. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | C.14 | Is station lighting sufficient and operational ? | Prévoir une remise en état de l'éclairage de la station. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.04c | If "NO", are there anti-siphon valves on the suction pipes of above-ground tanks? | Prévoir l'installation de clapets anti-siphon sur les tuyauteries des cuves aériennes. | N |  | 17 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | La date du dernier contrôle des extincteurs est-elle inférieure à 1 an? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | J.03 | Does the station have a first-aid kit? | La station dispose-t-elle d'une trousse de premier secours ? | N |  | 17 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | G.16 | Are the fire extinguishers in the bay sealed? | Les extincteurs de la baie sont-ils plombés ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boffa torodoya | GN111S0481 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 17 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 18 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | C.01 | Is the following signage present on forecourt islands: No smoking? | Prévoir la mise en place de pictogrammes "Défense de fumer" sur la piste. | N |  | 18 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | C.03 | Is the following signage present on forecourt islands: Engine shutdown required? | Prévoir la mise en place de pictogrammes "Arrêt du Moteur" sur la piste. | N |  | 18 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | C.14 | Is station lighting sufficient and operational ? | Prévoir une remise en état de l'éclairage de la station. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 18 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | C.02 | Is the following signage present on forecourt islands: Use of cell phone forbidden? | Prévoir la mise en place de pictogrammes "Téléphones Interdits" sur la piste. | N |  | 18 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | La date du dernier contrôle des extincteurs est-elle inférieure à 1 an? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | G.16 | Are the fire extinguishers in the bay sealed? | Les extincteurs de la baie sont-ils plombés ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 18 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Boke yomboya | GN111S0111 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 12 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | La base des appareils distributeurs est-elle propre, sans fuite de carburant apparente sur les îlots de distribution ? | N |  | 12 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Prévoir la mise en place d'un séparateur hydrocarbures piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Prévoir la mise en place de caniveaux et regards pour récupérer les eaux de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | C.10 | Is the offloading area connected to an oil separator? | Prévoir la mise en place d'un séparateur ou le raccordement de la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Prévoir la mise en place d'un système de traitement des eaux usées selon l'invariant ET03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Dalaba syli | GN111S0072 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 12 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | G.07 | Is the service bay also used for car washing? | La baie de services est-elle également utilisée pour faire du lavage auto ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Prévoir le raccordement des réservoirs du site au réseau de mise à la terre. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Fria economat | GN111S0062 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Prévoir la mise en place de pictogrammes "DANGER ÉLECTRIQUE" sur les installations. | N |  | 18 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | G.16 | Are the fire extinguishers in the bay sealed? | Les extincteurs de la baie sont-ils plombés ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | La date du dernier contrôle des extincteurs est-elle inférieure à 1 an? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Gbantama | GN111S0517 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 18 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | C.12b | Is the fire extinguisher inspection date less than 1 year old? | Prévoir un nouveau contrôle de l'ensemble des extincteurs du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 25 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 25 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 25 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | C.12a | Are the seals of all the fire extinguishers intact? | Les extincteurs sont-ils tous plombés correctement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | J.03 | Does the station have a first-aid kit? | La station dispose-t-elle d'une trousse de premier secours ? | N |  | 25 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 25 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar barrage | GN111S0063 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | C.02 | Is the following signage present on forecourt islands: Use of cell phone forbidden? | Prévoir la mise en place de pictogrammes "Téléphones Interdits" sur la piste. | N |  | 29 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | C.03 | Is the following signage present on forecourt islands: Engine shutdown required? | Prévoir la mise en place de pictogrammes "Arrêt du Moteur" sur la piste. | N |  | 29 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | B.09b | Is the date of the last inspection of all the site's fire extinguishers less than 1 year old? | Prévoir un nouveau contrôle de l'ensemble des matériels de protection incendie du site. | N |  | 29 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 29 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 29 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | C.01 | Is the following signage present on forecourt islands: No smoking? | Prévoir la mise en place de pictogrammes "Défense de fumer" sur la piste. | N |  | 29 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Prévoir la mise en place du "Réagir en Cas d'Urgence" sur site. | N |  | 29 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | G.12 | Is the bay inside lighting sufficient and operational? | Prévoir une remise en état de l'éclairage de la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar commisariat | GN111S0064 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | C.12b | Is the fire extinguisher inspection date less than 1 year old? | Prévoir un nouveau contrôle de l'ensemble des extincteurs du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 25 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 25 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | N |  | 25 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | C.12a | Are the seals of all the fire extinguishers intact? | Les extincteurs sont-ils tous plombés correctement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kamsar filima | GN111S0065 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Prévoir la mise en place de pictogrammes "DANGER ÉLECTRIQUE" sur les installations. | N |  | 25 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 12 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Prévoir la mise en place d'un système de traitement des eaux usées selon l'invariant ET03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia foulayah | GN111S0208 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 12 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.02 | Are the bay and its storage area clean, with a non-slip floor? | La baie et sa zone de stockage sont-elles propres avec un sol antidérapant ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Prévoir la mise en place d'un système de traitement des eaux usées selon l'invariant ET03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia gare routiere | GN111S0067 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 12 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Y a-t-il des équipements électriques (ex: moteur, pompe) placés à proximité d'une source d'eau ? | N |  | 12 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Prévoir la mise en place d'un système de traitement des eaux usées selon l'invariant ET03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Kindia samoroya | GN111S0068 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 27 May 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 27 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 27 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 27 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara assifate | GN111S0073 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 27 May 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 27 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Koundara donzo | GN111S0116 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 16 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 16 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 16 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 16 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Labe safatou | GN111S0074 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Prévoir la remise en état de la signalétique du tableau électrique de la station. | N |  | 18 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Faire réaliser une inspection complète des installations électriques du site par un bureau de contrôle agréé. | N |  | 18 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 18 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 18 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Le personnel de la station est-il informé des règles et obligations liées à la consignation électrique des équipements ? | N |  | 18 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Prévoir la mise en place de disjoncteurs différentiels 30 mA pour répondre à l'invariants ES07. | N |  | 18 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | B.15 | Do electrical disconnectors (circuit breakers, fuses) switch off all phases and neutral simultaneously? | Les coupes-circuits électriques (disjoncteurs, fusibles) coupent-ils simultanément toutes les phases et le neutre de l'installation ? | N |  | 18 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | N |  | 18 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | G.12 | Is the bay inside lighting sufficient and operational? | Prévoir une remise en état de l'éclairage de la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | C.14 | Is station lighting sufficient and operational ? | Prévoir une remise en état de l'éclairage de la station. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 18 May 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | H.01 | Is the flooring of the carwash areas non-slippery? | Le revêtement de sol des aires de lavage est-il antidérapant ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Prévoir la mise en place d'un système de traitement des eaux usées selon l'invariant ET03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 18 May 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou b | GN111S0077 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 19 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 19 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 19 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | J.01 | Does the station have a fire blanket? | Plan to install a fire blanket on the station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 19 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 19 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 19 May 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Plan to install a wastewater treatment system in accordance with invariant ET03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou c | GN111S0078 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | C.14 | Is station lighting sufficient and operational ? | Prévoir une remise en état de l'éclairage de la station. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 22 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | C.01 | Is the following signage present on forecourt islands: No smoking? | Prévoir la mise en place de pictogrammes "Défense de fumer" sur la piste. | N |  | 22 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 22 May 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou carrefour | GN111S0080 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Faire réaliser une inspection complète des installations électriques du site par un bureau de contrôle agréé. | N |  | 19 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 19 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 19 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Prévoir la mise en place de caniveaux et regards pour récupérer les eaux de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | C.10 | Is the offloading area connected to an oil separator? | Prévoir la mise en place d'un séparateur ou le raccordement de la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Prévoir le raccordement des réservoirs du site au réseau de mise à la terre. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Prévoir la mise en place d'un séparateur hydrocarbures piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | N |  | 19 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Prévoir la mise en place du "Réagir en Cas d'Urgence" sur site. | N |  | 19 Feb 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 19 May 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou d | GN111S0079 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 11 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | N |  | 11 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 11 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Mamou hoolo | GN111S0544 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 12 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Prévoir la mise en place d'un séparateur hydrocarbures piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Prévoir la mise en place de caniveaux et regards pour récupérer les eaux de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | C.10 | Is the offloading area connected to an oil separator? | Prévoir la mise en place d'un séparateur ou le raccordement de la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Prévoir la mise en place d'un système de traitement des eaux usées selon l'invariant ET03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita marketing | GN111S0119 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 12 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 12 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 12 Mar 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 12 Jun 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Pita parc | GN111S0081 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 28 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 28 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Prévoir la mise en place de caniveaux et regards pour récupérer les eaux de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | C.10 | Is the offloading area connected to an oil separator? | Prévoir la mise en place d'un séparateur ou le raccordement de la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | Si la baie est équipée de fosses, sont-elles toutes sécurisées à l'aide d'un caillebotis galvanisés ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Prévoir la mise en place du "Réagir en Cas d'Urgence" sur site. | N |  | 28 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 28 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 28 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Prévoir la mise en place d'un séparateur hydrocarbures piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Prévoir l'installation de rails chasse-roues pour sécuriser les fosses dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 28 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Sangaredi | GN111S0070 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | C.02 | Is the following signage present on forecourt islands: Use of cell phone forbidden? | Plan to install “Cell Phones Forbidden” pictograms on the forecourt. | N |  | 22 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | C.03 | Is the following signage present on forecourt islands: Engine shutdown required? | Plan to install “Engine Stop” pictograms on the forecourt. | N |  | 22 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.37 | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 22 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 22 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 22 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | C.01 | Is the following signage present on forecourt islands: No smoking? | Plan to install “No smoking” pictograms on the forecourt. | N |  | 22 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 22 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | J.01 | Does the station have a fire blanket? | Plan to install a fire blanket on the station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 22 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 22 Jan 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 22 Apr 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tanene | GN111S0071 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 27 May 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 27 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Telimele | GN111S0057 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Une mesure de résistance de la mise à la terre des installations de la station est-elle bien indiquée dans ce rapport ? Et est-elle bien inférieure à 10 ohms ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 28 Aug 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 28 May 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | N |  | 28 May 2025
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Guinée SA | Tougué | GN111S0446 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Autoroute péage | SN111S5026 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Autoroute péage | SN111S5026 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Autoroute péage | SN111S5026 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Autoroute péage | SN111S5026 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Autoroute péage | SN111S5026 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Autoroute péage | SN111S5026 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Autoroute péage | SN111S5026 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 07 Nov 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 07 Nov 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Bakel | SN111S3128 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Y a-t-il des équipements électriques (ex: moteur, pompe) placés à proximité d'une source d'eau ? | N |  | 17 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Prévoir la mise en place de caniveaux et regards pour récupérer les eaux de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 17 Jan 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | N |  | 17 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boucotte | SN111S3135 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boudody | SN111S3143 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Boustane Kaolack | SN111S5013 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Castors | SN111S3076 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Castors | SN111S3076 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Castors | SN111S3076 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Faire réaliser un raccordement à la terre visible sur les évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Castors | SN111S3076 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Castors | SN111S3076 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Castors | SN111S3076 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Castors | SN111S3076 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Castors | SN111S3076 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Castors | SN111S3076 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | El Mansour | SN111S3063 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | El Mansour | SN111S3063 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 21 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | El Mansour | SN111S3063 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | El Mansour | SN111S3063 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | El Mansour | SN111S3063 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 21 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | El Mansour | SN111S3063 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | El Mansour | SN111S3063 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Fanay Diery | SN111S3096 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Fanay Diery | SN111S3096 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Fanay Diery | SN111S3096 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Fanay Diery | SN111S3096 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Fanay Diery | SN111S3096 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Fanay Diery | SN111S3096 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Gokhou Mbathie | SN111S5137 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Gokhou Mbathie | SN111S5137 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Gokhou Mbathie | SN111S5137 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Gokhou Mbathie | SN111S5137 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Gokhou Mbathie | SN111S5137 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Gokhou Mbathie | SN111S5137 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Gokhou Mbathie | SN111S5137 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | Si la baie est équipée de fosses, sont-elles toutes sécurisées à l'aide d'un caillebotis galvanisés ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 17 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 17 Jan 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 17 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Kebemer | SN111S4178 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | E.06 | Are all the offloading coupling ports padlocked? | Les bouches de dépotage sont-elles toutes bien cadenassées ? | N |  | 16 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Prévoir une remise en état des caniveaux de la piste de distribution. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | Si la baie est équipée de fosses, sont-elles toutes sécurisées à l'aide d'un caillebotis galvanisés ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 16 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | C.14 | Is station lighting sufficient and operational ? | Prévoir une remise en état de l'éclairage de la station. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Grt Zinguinchor | SN111S5113 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 16 Jan 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Faire réaliser un raccordement à la terre visible sur les évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 21 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | D.17 | Do station staff have water paste on site to check the presence of water in the tanks? | Le personnel de la station dispose-t-il de pâte à eau sur site pour contrôler la présence d'eau dans les réservoirs ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | D.18 | Does the station staff carry out a daily check of fuel stocks, reconciling physical and accounting inventories? | L'exploitant fait-il un contrôle quotidien des stocks de carburants avec réconciliation des stocks physique et comptable ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | D.19 | Does the station manager monitor fuel losses: WetStock Management? | L'exploitant a-t-il un suivi des pertes carburants : WetStock Management ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Les employés de la station sont-il bien équipés des EPI réglementaires : gilet fluo + casque + chaussure de sécurité + gants + lunettes ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Prévoir la mise en place du "Réagir en Cas d'Urgence" sur site. | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 21 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Jardins | SN111S3060 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | E.06 | Are all the offloading coupling ports padlocked? | Les bouches de dépotage sont-elles toutes bien cadenassées ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Les bouches de dépotages sont-elles protégées à l'aide d'un musoir, d'un muret en béton ou de poteaux anti-bélier ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | La base des appareils distributeurs est-elle propre, sans fuite de carburant apparente sur les îlots de distribution ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Faire réaliser un raccordement à la terre visible sur les évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Le personnel de la station a-t-il connaissance des procédures de ticketing pour les intervention de maintenance en cas de panne d'un équipement sur site (DAISY WorldWide) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Les employés de la station sont-il bien équipés des EPI réglementaires : gilet fluo + casque + chaussure de sécurité + gants + lunettes ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Hann Plage | SN111S3056 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Faire réaliser un raccordement à la terre visible sur les évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs disposent-ils de systèmes de vérifications périodiques de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kafountine | SN111S3144 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 17 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 17 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Kebemer | SN111S3116 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Khar Yalla | SN111S3061 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Khar Yalla | SN111S3061 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Khar Yalla | SN111S3061 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Khar Yalla | SN111S3061 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Khar Yalla | SN111S3061 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Khar Yalla | SN111S3061 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Khar Yalla | SN111S3061 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 3m d'un ouverture, d'un point électrique, d'un point bas, de la limite de propriété du site ou la voie publique ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 21 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 21 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Lat Dior | SN111S5011 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Leona Kaolack | SN111S3153 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Leona Kaolack | SN111S3153 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation des détecteur de fuite de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Leona Kaolack | SN111S3153 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Leona Kaolack | SN111S3153 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Leona Kaolack | SN111S3153 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Leona Kaolack | SN111S3153 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Liberte 6 | SN111S3001 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Liberte 6 | SN111S3001 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Liberte 6 | SN111S3001 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Liberte 6 | SN111S3001 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | Si la baie est équipée de fosses, sont-elles toutes sécurisées à l'aide d'un caillebotis galvanisés ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 06 Nov 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Linguere | SN111S3113 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 06 Nov 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Dahra | SN111S4166 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Dahra | SN111S4166 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Prévoir le raccordement des réservoirs du site au réseau de mise à la terre. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Dahra | SN111S4166 | D.09 | Are manual gauging/dipping heads easily accessible to the station staff (maximum 30 cm below forecourt road cover)? | Les têtes de jaugeage manuel sont-elles faciles d'accès pour l'exploitant (maximum 30 cm sous le niveau du tampon de piste) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Faire réaliser un raccordement à la terre visible sur les évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 17 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 17 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Louga Rte de Potou | SN111S4115 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Medina Ndiathbe | SN111S5106 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Medina Ndiathbe | SN111S5106 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Medina Ndiathbe | SN111S5106 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Medina Ndiathbe | SN111S5106 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Medina Ndiathbe | SN111S5106 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ngor | SN111S3167 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Ngor | SN111S3167 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation des détecteur de fuite de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ngor | SN111S3167 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ngor | SN111S3167 | L.03 | Are the regulatory control stickers present and compliant on all EV chargers? | Les vignettes de contrôles réglementaires sont-elles bien présentes et conformes sur chacune des bornes de recharge ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ngor | SN111S3167 | L.08 | Is the lighting at the charging installation adequate and operational? | L'éclairage de l’aire de recharge est-il suffisant et opérationnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ngor | SN111S3167 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ngor | SN111S3167 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ngor | SN111S3167 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ngor | SN111S3167 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Nioro | SN111S3159 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Nioro | SN111S3159 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation des détecteur de fuite de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Nioro | SN111S3159 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Nioro | SN111S3159 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Nioro | SN111S3159 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Nioro | SN111S3159 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Omvs | SN111S5108 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Omvs | SN111S5108 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Omvs | SN111S5108 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Omvs | SN111S5108 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Omvs | SN111S5108 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Omvs | SN111S5108 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Omvs | SN111S5108 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 21 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 21 Oct 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ouakam Centre | SN111S3009 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | E.06 | Are all the offloading coupling ports padlocked? | Les bouches de dépotage sont-elles toutes bien cadenassées ? | N |  | 06 Aug 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Prévoir une rénovation de l'aire de dépotage. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Les bouches de dépotages sont-elles protégées à l'aide d'un musoir, d'un muret en béton ou de poteaux anti-bélier ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | L'aire de dépotage est-elle équipée d'un système de raccordement à la terre pour connecter le camion de livraison : piquet / pince / enrouleur ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ounare | SN111S4134 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | E.06 | Are all the offloading coupling ports padlocked? | Les bouches de dépotage sont-elles toutes bien cadenassées ? | N |  | 06 Aug 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Prévoir le raccordement des réservoirs du site au réseau de mise à la terre. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 06 Nov 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Prévoir une rénovation de l'aire de dépotage. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Les bouches de dépotages sont-elles protégées à l'aide d'un musoir, d'un muret en béton ou de poteaux anti-bélier ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | L'aire de dépotage est-elle équipée d'un système de raccordement à la terre pour connecter le camion de livraison : piquet / pince / enrouleur ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Ourossogui | SN111S3129 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 06 Nov 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Point E | SN111S3065 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Point E | SN111S3065 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Point E | SN111S3065 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Point E | SN111S3065 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Point E | SN111S3065 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Point E | SN111S3065 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Point E | SN111S3065 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rond Point Liberte X Vdn | SN111S3168 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Rond Point Liberte X Vdn | SN111S3168 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Rond Point Liberte X Vdn | SN111S3168 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Rond Point Liberte X Vdn | SN111S3168 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Rond Point Liberte X Vdn | SN111S3168 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Dakar | SN111S3084 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Prévoir la mise en place d'un séparateur hydrocarbures piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Dakar | SN111S3084 | C.10 | Is the offloading area connected to an oil separator? | Prévoir la mise en place d'un séparateur ou le raccordement de la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Dakar | SN111S3084 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur tous les compartiments de carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Dakar | SN111S3084 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation de détecteurs de fuites de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Dakar | SN111S3084 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Prévoir la mise en place d'un séparateur hydrocarbures piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | C.10 | Is the offloading area connected to an oil separator? | Prévoir la mise en place d'un séparateur ou le raccordement de la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur tous les compartiments de carburants du site. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | D.06a | Are these double-walled tanks equipped with leak detectors? | Prévoir l'installation de détecteurs de fuites de classe 2 sur tous les réservoirs double-parois. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | D.06b | Are the station's leak detection systems operational? | Prévoir la remise en état des détecteurs de fuites HS. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe et être conforme à l'EP06 | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure selon l'Invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Prévoir une remise en conformité du traitement des eaux de la baie selon l'Invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Rte de Khombole | SN111S3085 | J.07 | Is the station connected to the public wastewater network (sewers)? | Prévoir une mise en conformité des eaux usées du site, selon l'Invariant ET03 | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Prévoir la remise en état de la signalétique du tableau électrique de la station. | N |  | 16 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Prévoir la mise en place de pictogrammes "DANGER ÉLECTRIQUE" sur les installations. | N |  | 16 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Y a-t-il des équipements électriques (ex: moteur, pompe) placés à proximité d'une source d'eau ? | N |  | 16 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Faire remplacer les flexibles vétustes ou âgés de plus de 6 ans. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Santhiaba Ziguinchor | SN111S3138 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 16 Jan 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | C.14 | Is station lighting sufficient and operational ? | Prévoir une remise en état de l'éclairage de la station. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Faire réaliser un raccordement à la terre visible sur les évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs disposent-ils de systèmes de vérifications périodiques de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Sedhiou | SN111S5117 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Soumbedioune | SN111S3054 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Soweto | SN111S3052 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | E.06 | Are all the offloading coupling ports padlocked? | Les bouches de dépotage sont-elles toutes bien cadenassées ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Les bouches de dépotages sont-elles protégées à l'aide d'un musoir, d'un muret en béton ou de poteaux anti-bélier ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | L'aire de dépotage est-elle équipée d'un système de raccordement à la terre pour connecter le camion de livraison : piquet / pince / enrouleur ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | La base des appareils distributeurs est-elle propre, sans fuite de carburant apparente sur les îlots de distribution ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Faire réaliser un raccordement à la terre visible sur les évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Le personnel de la station a-t-il connaissance des procédures de ticketing pour les intervention de maintenance en cas de panne d'un équipement sur site (DAISY WorldWide) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | D.17 | Do station staff have water paste on site to check the presence of water in the tanks? | Le personnel de la station dispose-t-il de pâte à eau sur site pour contrôler la présence d'eau dans les réservoirs ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Les employés de la station sont-il bien équipés des EPI réglementaires : gilet fluo + casque + chaussure de sécurité + gants + lunettes ? | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Prévoir la mise en place du "Réagir en Cas d'Urgence" sur site. | N |  | 21 Jul 2025
AFR | AFO | TotalEnergies Marketing Sénégal | Yoff Tonghor | SN111S3030 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité conforme des tuyauteries pétrolières est-il disponible pour la station ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Mettre en conformité la distance des évents pour les rendre visibles du dépotage et se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Prévoir une remise en conformité complète de la signalétique du dépotage. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Prévoir une remise en état complète de la signalétique des évents. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs disposent-ils de systèmes de vérifications périodiques de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Prévoir une remise au propre de la signalétique produits sur les réservoirs. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 17 Jan 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | AFO | TotalEnergies Marketing Sénégal | Zinguinchor Escale | SN111S3136 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 22 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 22 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 22 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | H.04 | Is the lighting of washing areas sufficient and operational? | Plan to revamp the lighting in the carwash area. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Abattoirs | ET111S0072 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 14 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 14 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 14 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 14 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 14 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Arat Kilo | ET111S0042 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 15 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 15 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Menaheria Akabai | ET111S0246 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 15 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.07 | Is the service bay also used for car washing? | Is the service bay also used for car washing? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.26 | Are vent heads at least 4m high from the ground? | Raise vent heads to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa Piassa | ET111S0052 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | G.07 | Is the service bay also used for car washing? | Is the service bay also used for car washing? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02a | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02b | Does the affiliate have a specific system for monitoring, justifying and tracing fuel losses at service stations in writing?" | Set up a specific organization to monitor fuel losses at filling stations. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02e | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02f | Does the affiliate use a ticketing tool to track maintenance operations and fault resolution times? | Does the affiliate use a ticketing tool to track maintenance operations and fault resolution times? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Install PLLD (Pressurized Line Leak Detector) pressure sensors on all submersible pumps on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02l | Is the automatic gauging system interconnected to the dispensers to enable stock reconciliation and continuous leak detection? | Plan to install the dedicated management module in the automatic gauge. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are ALL the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 automatic gauge on the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.02p | Are prefabricated PE oiltight sumps installed below all dispensers on the pressurized site ? | Plan to install prefabricated PE oiltight sumps below all dispensers on the pressurized site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Awassa University Road | ET111S0381 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 14 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 14 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton dedicated to the forecourt and instantly accessible by station staff. | N |  | 14 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 14 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 14 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 14 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 14 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 14 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Ayat 1 | ET111S0399 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bethel | ET111S0401 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.07 | Is the service bay also used for car washing? | Is the service bay also used for car washing? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 06 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Bulgaria | ET111S0075 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Plan to install a wastewater treatment system in accordance with invariant ET03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 24 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Campo Asmara | ET111S0079 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 18 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 18 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | H.01 | Is the flooring of the carwash areas non-slippery? | Is the flooring of the carwash areas non-slippery? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 18 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 18 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 18 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 18 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Colson Street | ET111S0030 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.07 | Is the service bay also used for car washing? | Is the service bay also used for car washing? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Plan for a revamping of the offloading area. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Diredawa Megala | ET111S0023 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 28 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 28 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 28 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 28 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 28 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 28 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gojam Route | ET111S0082 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 17 Oct 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Gullele Medhanialem School | ET111S0012 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Installer et raccorder la zone de lavage à un séparateur hydrocarbure (Invariant ET02). | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Prévoir l'installation de rails chasse-roues pour sécuriser les fosses dans la baie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Les regards et caniveaux de récupération des eaux de la baie sont-il reliés à un séparateur hydrocarbure dédié (différent de celui de la piste / dépotage) ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 19 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.15 | Is there at least one ABC powder extinguisher in the bay? | A-t-on bien au moins un extincteurs à poudre ABC dans la baie ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.16 | Are the fire extinguishers in the bay sealed? | Les extincteurs de la baie sont-ils plombés ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | La date du dernier contrôle des extincteurs est-elle inférieure à 1 an? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harambe Fil Wuha | ET111S0015 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 02 Oct 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 02 Oct 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Harar Ras | ET111S0022 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.07 | Is the service bay also used for car washing? | Is the service bay also used for car washing? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.09 | Are manual gauging/dipping heads easily accessible to the station staff (maximum 30 cm below forecourt road cover)? | Are manual gauging/dipping heads easily accessible to the station staff (maximum 30 cm below forecourt road cover)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 02 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 02 Oct 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 02 Oct 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jijiga | ET111S0021 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Plan for a revamping of the offloading area. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | C.11a | Is there a shovel in every sandbox? | Is there a shovel in every sandbox? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 15 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | C.11b | Do all the sand boxes have a lid / cover? | Do all the sand boxes have a lid / cover? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | H.01 | Is the flooring of the carwash areas non-slippery? | Is the flooring of the carwash areas non-slippery? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 15 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | H.04 | Is the lighting of washing areas sufficient and operational? | Plan to revamp the lighting in the carwash area. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 15 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Awetu | ET111S0046 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 16 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 16 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 16 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 16 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 16 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.07 | Is the service bay also used for car washing? | Is the service bay also used for car washing? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | C.11b | Do all the sand boxes have a lid / cover? | Do all the sand boxes have a lid / cover? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 16 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 16 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | C.11a | Is there a shovel in every sandbox? | Is there a shovel in every sandbox? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02e | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02f | Does the affiliate use a ticketing tool to track maintenance operations and fault resolution times? | Does the affiliate use a ticketing tool to track maintenance operations and fault resolution times? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.09 | Are manual gauging/dipping heads easily accessible to the station staff (maximum 30 cm below forecourt road cover)? | Are manual gauging/dipping heads easily accessible to the station staff (maximum 30 cm below forecourt road cover)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 16 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.16 | Does the station have a graduated gauge ruler in good condition, allowing manual gauging to be carried out? | Provide a gauging ruler to the station. | N |  | 16 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02a | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02b | Does the affiliate have a specific system for monitoring, justifying and tracing fuel losses at service stations in writing?" | Set up a specific organization to monitor fuel losses at filling stations. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | H.04 | Is the lighting of washing areas sufficient and operational? | Plan to revamp the lighting in the carwash area. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 16 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 16 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 16 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 automatic gauge on the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02n | Are there shear valves, firmly fixed to the dispensing islands, at the feet of all dispensers? | Install breakaway shear valves at the feet of all dispensers. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02p | Are prefabricated PE oiltight sumps installed below all dispensers on the pressurized site ? | Plan to install prefabricated PE oiltight sumps below all dispensers on the pressurized site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Install PLLD (Pressurized Line Leak Detector) pressure sensors on all submersible pumps on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02l | Is the automatic gauging system interconnected to the dispensers to enable stock reconciliation and continuous leak detection? | Plan to install the dedicated management module in the automatic gauge. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are ALL the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Jimma Teka Hotel | ET111S0043 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Implement the LockOut - TagOut procedures for the maintenance of pressurized sites and inform the station staff. | N |  | 16 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker upstream of electrical installations. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 03 Jul 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 03 Jan 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 03 Jan 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | D.06 | Are all the station's fuel tanks double-walled? | Plan for the replacement of the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Falogora | ET111S0041 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 03 Jul 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Gelan | ET111S0406 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Gelan | ET111S0406 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Gelan | ET111S0406 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Gelan | ET111S0406 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 18 Dec 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Gelan | ET111S0406 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Gelan | ET111S0406 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 18 Dec 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Gelan | ET111S0406 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 18 Dec 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Kality Gelan | ET111S0406 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton dedicated to the forecourt and instantly accessible by station staff. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.02a | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.02e | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 15 Aug 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 15 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 automatic gauge on the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.02n | Are there shear valves, firmly fixed to the dispensing islands, at the feet of all dispensers? | Install breakaway shear valves at the feet of all dispensers. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 15 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 15 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.02p | Are prefabricated PE oiltight sumps installed below all dispensers on the pressurized site ? | Plan to install prefabricated PE oiltight sumps below all dispensers on the pressurized site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.02l | Is the automatic gauging system interconnected to the dispensers to enable stock reconciliation and continuous leak detection? | Plan to install the dedicated management module in the automatic gauge. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are ALL the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Lamberet | ET111S0036 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Implement the LockOut - TagOut procedures for the maintenance of pressurized sites and inform the station staff. | N |  | 15 Nov 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 09 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 09 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 09 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Amanuel | ET111S0014 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 09 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 09 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | G.07 | Is the service bay also used for car washing? | Is the service bay also used for car washing? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 09 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Merkato Shenkora Berenda | ET111S0013 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 24 Jun 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | C.08b | If “YES”, are these gutters and water drainage tight and in good condition? | Plan to restore the gutters on the forecourt area. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | H.04 | Is the lighting of washing areas sufficient and operational? | Plan to revamp the lighting in the carwash area. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Meskel Square | ET111S0037 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters to collect water from the forecourt and send it to a separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 or DOVER PROGAUGE ATG on the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.02l | Is the automatic gauging system interconnected to the dispensers to enable stock reconciliation and continuous leak detection? | Plan to install the dedicated management module in the automatic gauge. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.02p | Are prefabricated PE oiltight sumps installed below all dispensers on the pressurized site ? | Plan to install prefabricated PE oiltight sumps below all dispensers on the pressurized site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 30 Jun 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 30 Dec 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading area into compliance with the Invariant EP10. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Plan to upgrade the fuel pipes to comply with the EP11 invariant compensatory measure. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.06 | Are all the station's fuel tanks double-walled? | Plan for the replacement of the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Minilque Square | ET111S0029 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 30 Jun 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Install fire extinguishers in the bay to comply with Invariants ES01. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 13 Dec 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 Jun 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Nifas Silk | ET111S0038 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 28 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 28 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 28 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 28 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 28 Jul 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Partiors Sebara Babur | ET111S0028 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 05 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Is there at least one ABC powder extinguisher in the bay? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.16 | Are the fire extinguishers in the bay sealed? | Are the fire extinguishers in the bay sealed? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | Is the date of the last fire extinguisher inspection less than 1 year old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 05 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 05 Sep 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.07 | Is the service bay also used for car washing? | Is the service bay also used for car washing? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Sebategna Merkato | ET111S0001 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 30 Dec 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker upstream of electrical installations. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 30 Dec 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 30 Jun 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 30 Dec 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 30 Dec 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 30 Dec 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Plan for renovation of the offloading area in line with invariant EP10. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading area into compliance with the Invariant EP10. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 30 Dec 2025
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 30 Jun 2026
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Plan to bring offloading area into compliance with invariant EP10. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Ethiopia S.C | Shashemene Alaba Mazoria | ET111S0051 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Connect the offloading couplings to the site's grounding system in a visible manner, in accordance with Invariant ES02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Le personnel de la station est-il informé des règles et obligations liées à la consignation électrique des équipements ? | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 11 Oct 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 11 Oct 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Avaradoha | MG111SAVAR | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Le personnel de la station est-il informé des règles et obligations liées à la consignation électrique des équipements ? | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Prévoir la mise en place d'un extincteur CO2 dédié aux feux d'origine électrique à proximité de chaque coffret électriques du site. | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 11 Oct 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 11 Oct 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 11 Oct 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Balisama | MG111SBALI | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | N |  | 19 Sep 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Prévoir une remise en état du tableau électrique de la station. | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Une mesure de résistance de la mise à la terre des installations de la station est-elle bien indiquée dans ce rapport ? Et est-elle bien inférieure à 10 ohms ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Le personnel de la station est-il informé des règles et obligations liées à la consignation électrique des équipements ? | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Prévoir l'installation de rails chasse-roues pour sécuriser les fosses dans la baie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 19 Sep 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | G.20 | Is used oil collected and properly treated? | Les huiles usées sont-elles collectées et traitées correctement ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | Dans le cadre de la solarisation de la station, une étude de structure a-t-elle bien été réalisée pour chaque structure recevant des modules PV ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 19 Sep 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 19 Sep 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Kianja | MG111SKIAN | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 19 Dec 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | N |  | 19 Sep 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Prévoir une remise en état du tableau électrique de la station. | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | G.05 | Is the pits and bay drainage system operational and in good condition? | L''évacuation des eaux et résidus des fosses et de la baie est-elle opérationnelle et en bon état ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Les portiques et autres équipements mobiles de lavage sont-ils tous correctement positionnés pour éviter tout risque d'écrasement en fonctionnement ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 19 Sep 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 19 Sep 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Prévoir la réalisation d'une réépreuve des cuves simple-enveloppe du site. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Madera | MG111SMADE | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Mahery | MG111SMAHE | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Le personnel de la station est-il informé des règles et obligations liées à la consignation électrique des équipements ? | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Mahery | MG111SMAHE | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 19 Jun 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Mahery | MG111SMAHE | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Mahery | MG111SMAHE | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Mahery | MG111SMAHE | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Mahery | MG111SMAHE | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Mahery | MG111SMAHE | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Mahery | MG111SMAHE | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Mahery | MG111SMAHE | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 19 Sep 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Le personnel de la station est-il informé des règles et obligations liées à la consignation électrique des équipements ? | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 11 Oct 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 11 Oct 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ny Antsika | MG111ANTK | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Soanierana | MG111SSOAN | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Soanierana | MG111SSOAN | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Soanierana | MG111SSOAN | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 21 May 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Soanierana | MG111SSOAN | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Soanierana | MG111SSOAN | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Les employés de la station sont-il bien équipés des EPI réglementaires : gilet fluo + casque + chaussure de sécurité + gants + lunettes ? | N |  | 21 May 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Soanierana | MG111SSOAN | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Prévoir le raccordement des installations PV sur l'arrêt d'urgence piste de la station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Soanierana | MG111SSOAN | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | Dans le cadre de la solarisation de la station, une étude de structure a-t-elle bien été réalisée pour chaque structure recevant des modules PV ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Soanierana | MG111SSOAN | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | B.13a | Is this generator equipped with an automatic source inverter? | Prévoir la mise en place d'une procédure de permutation à vide pour l'utilisation de l'inverseur de source manuel du site. | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Le personnel de la station est-il informé des règles et obligations liées à la consignation électrique des équipements ? | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Prévoir la mise en place d'un extincteur CO2 dédié aux feux d'origine électrique à proximité de chaque coffret électriques du site. | N |  | 11 Jul 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 11 Oct 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 11 Oct 2025
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Madagasikara S.A. | Ss Volombato | MG111SVOLO | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Aerodrome | MA111S4565 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | Y | Zouhair BOUFRACHA | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Aerodrome | MA111S4565 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Aerodrome | MA111S4565 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Zouhair BOUFRACHA | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Prévoir la mise en place de disjoncteurs différentiels 30 mA pour répondre à l'invariants ES07. | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | E.03 | Is the offloading area oil-tight? | L'aire de dépotage est-elle étanche aux hydrocarbures? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Les bouches de dépotages sont-elles protégées à l'aide d'un musoir, d'un muret en béton ou de poteaux anti-bélier ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | La base des appareils distributeurs est-elle propre, sans fuite de carburant apparente sur les îlots de distribution ? | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Prévoir la mise en place d'un séparateur hydrocarbures piste. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Prévoir la création de musoirs béton sur les îlots pour protéger les appareils distributeurs. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | C.14 | Is station lighting sufficient and operational ? | Prévoir une remise en état de l'éclairage de la station. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Prévoir la mise en place d'un disjoncteur différentiel 300mA en tête du tableau électrique. | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Prévoir la remise en état de la signalétique du tableau électrique de la station. | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | N |  | 06 Sep 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Prévoir une remise en état du tableau électrique de la station. | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Prévoir l'obturation des fourreaux électriques pour éviter les problème de vapeurs. | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Installer un séparateur ou relier la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.15 | Are the calibration charts of each tank available on site and still valid? | Fournir les barèmes de jaugeage à la station. | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 06 Sep 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Prévoir la mise en place de caniveaux et regards pour récupérer les eaux de la piste. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | C.10 | Is the offloading area connected to an oil separator? | Prévoir la mise en place d'un séparateur ou le raccordement de la zone de dépotage au séparateur de la piste. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.18 | Does the station staff carry out a daily check of fuel stocks, reconciling physical and accounting inventories? | L'exploitant fait-il un contrôle quotidien des stocks de carburants avec réconciliation des stocks physique et comptable ? | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.19 | Does the station manager monitor fuel losses: WetStock Management? | L'exploitant a-t-il un suivi des pertes carburants : WetStock Management ? | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | N |  | 06 Jun 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 06 Sep 2025
AFR | MOI | TotalEnergies Marketing Maroc | Affourer | MA111S2284 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Ain Harrouda | MA111S2238 | C.14 | Is station lighting sufficient and operational ? | Prévoir une remise en état de l'éclairage de la station. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Ain Harrouda | MA111S2238 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Un contrôle de bon fonctionnement des têtes d'évents datant de moins de 5 ans est-il disponible ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Ain Harrouda | MA111S2238 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Ain Harrouda | MA111S2238 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Ain Harrouda | MA111S2238 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | Y | Zouhair BOUFRACHA | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Ain Harrouda | MA111S2238 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Atlantis | MA111S4529 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Atlantis | MA111S4529 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Atlantis | MA111S4529 | L.03 | Are the regulatory control stickers present and compliant on all EV chargers? | Les vignettes de contrôles réglementaires sont-elles bien présentes et conformes sur chacune des bornes de recharge ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Atlantis | MA111S4529 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 13 Sep 2025
AFR | MOI | TotalEnergies Marketing Maroc | Atlantis | MA111S4529 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Atlantis | MA111S4529 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Atlantis | MA111S4529 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Atlantis | MA111S4529 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 13 Sep 2025
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Le camion de livraison carburant peut-il accéder à l'aire de dépotage en marche avant, sans manœuvre ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Le camion de livraison de carburants peut-il quitter l'aire dépotage en marche avant, sans manoeuvre ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 06 Sep 2025
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Beni Mellal | MA111S2290 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Calabonita | MA111S4263 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Relais Al Baida | MA111S3229 | K.02 | Are the photovoltaic systems located on the canopy or a shading roof? | Les installations photovoltaïques sont-elles situées sur l'auvent ou une ombrière ? | Y | Zouhair BOUFRACHA | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Relais Al Baida | MA111S3229 | K.19 | Is the station equipped with batteries? | L'installation PV est-elle équipée de batteries ? | Y | Zouhair BOUFRACHA | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Relais Al Baida | MA111S3229 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Prévoir la mise en conformité des dépotage pour se conformer à l'invariant EP10. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Relais Al Baida | MA111S3229 | K.03 | Are photovoltaic installations located on the station building? | Les installations photovoltaïques sont-elles situées sur un bâtiment du site ? | Y | Zouhair BOUFRACHA | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Tadla | MA111S4415 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Tadla | MA111S4415 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 06 Sep 2025
AFR | MOI | TotalEnergies Marketing Maroc | Tadla | MA111S4415 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Tadla | MA111S4415 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Tadla | MA111S4415 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Tadla | MA111S4415 | D.23 | Is there a compliant pipe integrity test report available for this station? | Un contrôle d'étanchéité datant de moins de 10 ans est-il disponible pour les tuyauteries pétrolières ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Tadla | MA111S4415 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Tadla | MA111S4415 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Tadla | MA111S4415 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Réaliser la levée des anomalies présentes dans le rapport de contrôle des installations électriques. | N |  | 06 Sep 2025
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 02 Nov 2025
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | J.08 | Are food products stored separately from non-food products? | Le stockage des produits alimentaires est-il physiquement bien séparé des produits non alimentaires? | N |  | 02 Aug 2025
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 02 Nov 2025
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Maroc | Temara | MA111S4402 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | C.11a | Is there a shovel in every sandbox? | Is there a shovel in every sandbox? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | D.02d | Is there a maintenance contract dedicated to pressurized installations with submersible pumps ? | Plan to set up a maintenance contract dedicated to pressuried sites equipped with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | D.02b | Does the affiliate have a specific system for monitoring, justifying and tracing fuel losses at service stations in writing?" | Set up a specific organization to monitor fuel losses at filling stations. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | D.02e | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 automatic gauge on the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 11 Outubro BP | MZ111S2264 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | E.11a | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 13 Jan 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | 25 De Setembro | MZ111S1202 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.02b | Does the affiliate have a specific system for monitoring, justifying and tracing fuel losses at service stations in writing?" | Set up a specific organization to monitor fuel losses at filling stations. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.02d | Is there a maintenance contract dedicated to pressurized installations with submersible pumps ? | Plan to set up a maintenance contract dedicated to pressuried sites equipped with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.02e | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Install PLLD (Pressurized Line Leak Detector) pressure sensors on all submersible pumps on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 automatic gauge on the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.02l | Is the automatic gauging system interconnected to the dispensers to enable stock reconciliation and continuous leak detection? | Plan to install the dedicated management module in the automatic gauge. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Is there a forced-running mode for submersible pumps, known and available to station staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.02p | Are prefabricated PE oiltight sumps installed below all dispensers on the pressurized site ? | Plan to install prefabricated PE oiltight sumps below all dispensers on the pressurized site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Caia | MZ111S2237 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | D.02a | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | D.02h | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Cmc BP | MZ111S2259 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 13 Jan 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | F.02e | Are all LPG cylinders (full and empty) stored on racks? | Are all LPG cylinders (full and empty) stored on racks? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka | MZ111S2233 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 14 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 14 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 14 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 14 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 14 Jan 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Intaka Village | MZ111S2244 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | B.15 | Do electrical disconnectors (circuit breakers, fuses) switch off all phases and neutral simultaneously? | Do electrical disconnectors (circuit breakers, fuses) switch off all phases and neutral simultaneously? | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | E.11a | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Plan to install a wastewater treatment system in accordance with invariant ET03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 13 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Km 11.5 | MZ111S2222 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Kumbeza | MZ111S2232 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Kumbeza | MZ111S2232 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Kumbeza | MZ111S2232 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Kumbeza | MZ111S2232 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Kumbeza | MZ111S2232 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.02a | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.02b | Does the affiliate have a specific system for monitoring, justifying and tracing fuel losses at service stations in writing?" | Set up a specific organization to monitor fuel losses at filling stations. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Install PLLD (Pressurized Line Leak Detector) pressure sensors on all submersible pumps on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are all the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Machava 15 BP | MZ111S2261 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | A.11b | If “YES”, is there a specific procedure for intervening near these power lines, and is it known by the station staff? | If “YES”, is there a specific procedure for intervening near these power lines, and is it known by the station staff? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.02a | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.02h | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are all the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Is there a forced-running mode for submersible pumps, known and available to station staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Macia BP | MZ111S2248 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 14 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 14 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 14 Jan 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga | MZ111S2208 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton dedicated to the forecourt and instantly accessible by station staff. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | A.11b | If “YES”, is there a specific procedure for intervening near these power lines, and is it known by the station staff? | If “YES”, is there a specific procedure for intervening near these power lines, and is it known by the station staff? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.02a | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.02b | Does the affiliate have a specific system for monitoring, justifying and tracing fuel losses at service stations in writing?" | Set up a specific organization to monitor fuel losses at filling stations. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.02h | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are all the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Mainga BP | MZ111S2249 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Matola Gare | MZ111S2234 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.02b | Does the affiliate have a specific system for monitoring, justifying and tracing fuel losses at service stations in writing?" | Set up a specific organization to monitor fuel losses at filling stations. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.02d | Is there a maintenance contract dedicated to pressurized installations with submersible pumps ? | Plan to set up a maintenance contract dedicated to pressuried sites equipped with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.02e | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Install PLLD (Pressurized Line Leak Detector) pressure sensors on all submersible pumps on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.02l | Is the automatic gauging system interconnected to the dispensers to enable stock reconciliation and continuous leak detection? | Plan to install the dedicated management module in the automatic gauge. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Is there a forced-running mode for submersible pumps, known and available to station staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 automatic gauge on the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.02p | Are prefabricated PE oiltight sumps installed below all dispensers on the pressurized site ? | Plan to install prefabricated PE oiltight sumps below all dispensers on the pressurized site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Muxungue BP | MZ111S2265 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Nacala BP | MZ111S2269 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Nacala BP | MZ111S2269 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Nacala BP | MZ111S2269 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Nacala BP | MZ111S2269 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Nampula BP | MZ111S2270 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Nampula BP | MZ111S2270 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Nampula BP | MZ111S2270 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Nampula BP | MZ111S2270 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Nampula BP | MZ111S2270 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Plan to upgrade the station's electrical board. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.09 | Are manual gauging/dipping heads easily accessible to the station staff (maximum 30 cm below forecourt road cover)? | Are manual gauging/dipping heads easily accessible to the station staff (maximum 30 cm below forecourt road cover)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Adjust vent distance to make them visible from the offloading and comply with invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Does the station have showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Niaa Petroleo | MZ111S2301 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Install a CO2 extinguisher dedicated to electrical fires near each electrical box on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.02d | Is there a maintenance contract dedicated to pressurized installations with submersible pumps ? | Plan to set up a maintenance contract dedicated to pressuried sites equipped with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.02b | Does the affiliate have a specific system for monitoring, justifying and tracing fuel losses at service stations in writing?" | Set up a specific organization to monitor fuel losses at filling stations. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.02e | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Install PLLD (Pressurized Line Leak Detector) pressure sensors on all submersible pumps on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.02l | Is the automatic gauging system interconnected to the dispensers to enable stock reconciliation and continuous leak detection? | Plan to install the dedicated management module in the automatic gauge. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 automatic gauge on the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Is there a forced-running mode for submersible pumps, known and available to station staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.02p | Are prefabricated PE oiltight sumps installed below all dispensers on the pressurized site ? | Plan to install prefabricated PE oiltight sumps below all dispensers on the pressurized site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Ofir BP | MZ111S2267 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Polana | MZ111S2210 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 20 Jun 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Salamanga | MZ111S2245 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 14 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Salamanga | MZ111S2245 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Salamanga | MZ111S2245 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Salamanga | MZ111S2245 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Salamanga | MZ111S2245 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Salamanga | MZ111S2245 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Salamanga | MZ111S2245 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Salamanga | MZ111S2245 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Salamanga | MZ111S2245 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Shoprite Pemba | MZ111S2246 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Shoprite Pemba | MZ111S2246 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Shoprite Pemba | MZ111S2246 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Shoprite Pemba | MZ111S2246 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | C.12 | Is the forecourt equipped with one ABC powder extinguisher per island? | Provide one ABC extinguisher per forecourt distribution island. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.02 | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | Is the service station a pressurized installation with submersible pumps located at the level of the manhole plates of the fuel tanks? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.02a | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.02d | Is there a maintenance contract dedicated to pressurized installations with submersible pumps ? | Plan to set up a maintenance contract dedicated to pressuried sites equipped with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.02e | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.15 | Are the calibration charts of each tank available on site and still valid? | Provide tanks calibration charts to the station. | N |  | 20 Mar 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Is there a check on the correct operation of vent heads that is less than 5 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.02h | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are all the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Tavele BP | MZ111S2247 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Via R#Pida | MZ111S2213 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Via R#Pida | MZ111S2213 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Do these overfill protection devices have systems for periodic verification of proper operation? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Via R#Pida | MZ111S2213 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 26 Aug 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Via R#Pida | MZ111S2213 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Via R#Pida | MZ111S2213 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 14 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | N |  | 14 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | N |  | 14 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 14 Oct 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 14 Jul 2025
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 14 Jan 2026
AFR | MOI | TotalEnergies Marketing Moçambique SA | Xai-Xai | MZ111S2211 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Boulevard Doret | RE111S0016 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Réunion | Boulevard Doret | RE111S0016 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Boulevard Doret | RE111S0016 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Réunion | Boulevard Doret | RE111S0016 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Boulevard Doret | RE111S0016 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Boulevard Doret | RE111S0016 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Boulevard Doret | RE111S0016 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Bras Panon | RE111S0030 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Bras Panon | RE111S0030 | L.05 | Are protective bollards installed in front of each EV chargers? | Installer des potelets de protection devant chaque borne EV. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Bras Panon | RE111S0030 | L.06 | There are no fire extinguishers in the immediate vicinity of the recharging area? | Prévoir d'enlever les extincteurs à proximité des bornes EV pour éviter tout problème en cas d'incendie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Bras Panon | RE111S0030 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Bras Panon | RE111S0030 | L.03 | Are the regulatory control stickers present and compliant on all EV chargers? | Les vignettes de contrôles réglementaires sont-elles bien présentes et conformes sur chacune des bornes de recharge ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Bras Panon | RE111S0030 | L.10 | Does the EV Charging Installations have a dedicated emergency stop device? | La zone IRVE dispose-t-elle d’un dispositif d’arrêt d’urgence dédié ? | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Réunion | Butor | RE111S0022 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Butor | RE111S0022 | L.06 | There are no fire extinguishers in the immediate vicinity of the recharging area? | Prévoir d'enlever les extincteurs à proximité des bornes EV pour éviter tout problème en cas d'incendie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Butor | RE111S0022 | L.03 | Are the regulatory control stickers present and compliant on all EV chargers? | Les vignettes de contrôles réglementaires sont-elles bien présentes et conformes sur chacune des bornes de recharge ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Cambuston | RE111S0001 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Cambuston | RE111S0001 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Réunion | Cambuston | RE111S0001 | L.05 | Are protective bollards installed in front of each EV chargers? | Installer des potelets de protection devant chaque borne EV. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Cambuston | RE111S0001 | L.06 | There are no fire extinguishers in the immediate vicinity of the recharging area? | Prévoir d'enlever les extincteurs à proximité des bornes EV pour éviter tout problème en cas d'incendie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Cambuston | RE111S0001 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Cambuston | RE111S0001 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Cambuston | RE111S0001 | L.03 | Are the regulatory control stickers present and compliant on all EV chargers? | Les vignettes de contrôles réglementaires sont-elles bien présentes et conformes sur chacune des bornes de recharge ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Cambuston | RE111S0001 | L.10 | Does the EV Charging Installations have a dedicated emergency stop device? | La zone IRVE dispose-t-elle d’un dispositif d’arrêt d’urgence dédié ? | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Réunion | Cambuston | RE111S0001 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 16 Jul 2025
AFR | MOI | TotalEnergies Marketing Réunion | Clinique | RE111S0021 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Clinique | RE111S0021 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Clinique | RE111S0021 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | La Marine | RE111S0047 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Prévoir la mise en conformité des installations photovoltaïques pour être conforme à l'invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | La Marine | RE111S0047 | L.06 | There are no fire extinguishers in the immediate vicinity of the recharging area? | Prévoir d'enlever les extincteurs à proximité des bornes EV pour éviter tout problème en cas d'incendie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | La Marine | RE111S0047 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | La Marine | RE111S0047 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | La Marine | RE111S0047 | L.03 | Are the regulatory control stickers present and compliant on all EV chargers? | Les vignettes de contrôles réglementaires sont-elles bien présentes et conformes sur chacune des bornes de recharge ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Lacaussade | RE111S0014 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Réunion | Lacaussade | RE111S0014 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Lacaussade | RE111S0014 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Lacaussade | RE111S0014 | L.06 | There are no fire extinguishers in the immediate vicinity of the recharging area? | Remove fire extinguishers from the vicinity of EV charging points to avoid problems in the event of fire. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Lacaussade | RE111S0014 | L.03 | Are the regulatory control stickers present and compliant on all EV chargers? | Are the regulatory control stickers present and compliant on all EV chargers? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Lacaussade | RE111S0014 | L.10 | Does the EV Charging Installations have a dedicated emergency stop device? | Does the EV Charging Installations have a dedicated emergency stop device? | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Réunion | Le Gol | RE111S2041 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Le Gol | RE111S2041 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Le Gol | RE111S2041 | D.19 | Does the station manager monitor fuel losses: WetStock Management? | L'exploitant a-t-il un suivi des pertes carburants : WetStock Management ? | N |  | 27 Feb 2025
AFR | MOI | TotalEnergies Marketing Réunion | Les Cafés | RE111S0025 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Les Cafés | RE111S0025 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Réunion | Les Cafés | RE111S0025 | L.05 | Are protective bollards installed in front of each EV chargers? | Installer des potelets de protection devant chaque borne EV. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Les Cafés | RE111S0025 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Les Cafés | RE111S0025 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Les Cafés | RE111S0025 | L.03 | Are the regulatory control stickers present and compliant on all EV chargers? | Les vignettes de contrôles réglementaires sont-elles bien présentes et conformes sur chacune des bornes de recharge ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Les Cafés | RE111S0025 | L.10 | Does the EV Charging Installations have a dedicated emergency stop device? | La zone IRVE dispose-t-elle d’un dispositif d’arrêt d’urgence dédié ? | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Réunion | Moufia | RE111S0020 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Moufia | RE111S0020 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Moufia | RE111S0020 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Providence | RE111S0012 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Providence | RE111S0012 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Prévoir le remplacement des tampons de piste par des tampons tampons en composite. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Réunion | Providence | RE111S0012 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Providence | RE111S0012 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Saint-André | RE111S0004 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Saint-André | RE111S0004 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 15 Apr 2025
AFR | MOI | TotalEnergies Marketing Réunion | Saint-André | RE111S0004 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Installer un extincteur CO2 à proximité immédiate du panneau électrique du groupe électrogène. | N |  | 15 Apr 2025
AFR | MOI | TotalEnergies Marketing Réunion | Saint-André | RE111S0004 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Saint-André | RE111S0004 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Saint-André | RE111S0004 | L.03 | Are the regulatory control stickers present and compliant on all EV chargers? | Les vignettes de contrôles réglementaires sont-elles bien présentes et conformes sur chacune des bornes de recharge ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Saint-Benoit | RE111S0019 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Saint-Benoit | RE111S0019 | L.03 | Are the regulatory control stickers present and compliant on all EV chargers? | Les vignettes de contrôles réglementaires sont-elles bien présentes et conformes sur chacune des bornes de recharge ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Saint-Benoit | RE111S0019 | L.10 | Does the EV Charging Installations have a dedicated emergency stop device? | La zone IRVE dispose-t-elle d’un dispositif d’arrêt d’urgence dédié ? | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Réunion | Saint-Benoit | RE111S0019 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Saint-Benoit | RE111S0019 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Réunion | Saint-Benoit | RE111S0019 | L.04 | Is there a valid QR Code on each EV charger that redirect to the correct EV Charge platform link? | A-t-on bien un QR Code en bon état sur chaque borne qui renvoie vers la plateforme EV Charge ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Saint-Benoit | RE111S0019 | L.05 | Are protective bollards installed in front of each EV chargers? | Installer des potelets de protection devant chaque borne EV. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Sainte-Suzanne | RE111S0011 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Sainte-Suzanne | RE111S0011 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Sainte-Suzanne | RE111S0011 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 24 Jul 2025
AFR | MOI | TotalEnergies Marketing Réunion | Trois Mares | RE111S0028 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | La base des appareils distributeurs est-elle propre, sans fuite de carburant apparente sur les îlots de distribution ? | N |  | 27 Feb 2025
AFR | MOI | TotalEnergies Marketing Réunion | Trois Mares | RE111S0028 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Trois Mares | RE111S0028 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs font-ils l'objet d'un contrôle périodique de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Trois Mares | RE111S0028 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Trois Mares | RE111S0028 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 27 May 2025
AFR | MOI | TotalEnergies Marketing Réunion | Zup Le Port | RE111S0018 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Zup Le Port | RE111S0018 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Zup Le Port | RE111S0018 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Réunion | Zup Le Port | RE111S0018 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | La station est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Réunion | Zup Le Port | RE111S0018 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Prévoir la réalisation par un bureau de contrôle d'une étude technique dédiée à l'amiante sur le site. | N |  | 24 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | G.07 | Is the service bay also used for car washing? | La baie de services est-elle également utilisée pour faire du lavage auto ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | N |  | 09 Aug 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Y a-t-il des équipements électriques (ex: moteur, pompe) placés à proximité d'une source d'eau ? | N |  | 09 Aug 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Bab Allouj | TN111S2232 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | B.07a | Are station staff informed of the rules and obligations relating to the electrical lockout/tagout of equipment? | Le personnel de la station est-il informé des règles et obligations liées à la consignation électrique des équipements ? | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Y a-t-il des équipements électriques (ex: moteur, pompe) placés à proximité d'une source d'eau ? | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Prévoir la mise en place d'un extincteur CO2 dédié aux feux d'origine électrique à proximité de chaque coffret électriques du site. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Prévoir l'installation de limiteurs de remplissage sur toutes les cuves carburants du site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 3m d'un ouverture, d'un point électrique, d'un point bas, de la limite de propriété du site ou la voie publique ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Prévoir la remise en état de la signalétique du tableau électrique de la station. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Prévoir la mise en place de pictogrammes "DANGER ÉLECTRIQUE" sur les installations. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Les installations électriques sont-elles dans un état général satisfaisant (vétusté, câblage, installations provisoires, état des disjoncteurs) ? | N |  | 17 Oct 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Prévoir les travaux de mise en conformité des installations électriques afin de supprimer les installations électriques provisoires du site. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | B.11 | Is all electrical board wiring protected from any contact (door, box, cover, faceplate, etc.)? | Prévoir une remise en état du tableau électrique de la station. | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.15 | Is there at least one ABC powder extinguisher in the bay? | A-t-on bien au moins un extincteurs à poudre ABC dans la baie ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.16 | Are the fire extinguishers in the bay sealed? | Les extincteurs de la baie sont-ils plombés ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | La date du dernier contrôle des extincteurs est-elle inférieure à 1 an? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Prévoir la mise en conformité des installations photovoltaïques pour être conforme à l'invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | L.04 | Is there a valid QR Code on each EV charger that redirect to the correct EV Charge platform link? | A-t-on bien un QR Code en bon état sur chaque borne qui renvoie vers la plateforme EV Charge ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | L.06 | There are no fire extinguishers in the immediate vicinity of the recharging area? | Prévoir d'enlever les extincteurs à proximité des bornes EV pour éviter tout problème en cas d'incendie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 17 Jan 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Les portiques et autres équipements mobiles de lavage sont-ils tous correctement positionnés pour éviter tout risque d'écrasement en fonctionnement ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | H.04 | Is the lighting of washing areas sufficient and operational? | Prévoir une remise en état de l'éclairage de la zone de lavage. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | N |  | 17 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.12 | Is the bay inside lighting sufficient and operational? | Prévoir une remise en état de l'éclairage de la baie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | L.03 | Are the regulatory control stickers present and compliant on all EV chargers? | Les vignettes de contrôles réglementaires sont-elles bien présentes et conformes sur chacune des bornes de recharge ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | L.10 | Does the EV Charging Installations have a dedicated emergency stop device? | La zone IRVE dispose-t-elle d’un dispositif d’arrêt d’urgence dédié ? | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Beja Gp6 | TN111S2219 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 08 Aug 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | Si la baie est équipée de fosses, sont-elles toutes sécurisées à l'aide d'un caillebotis galvanisés ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | G.07 | Is the service bay also used for car washing? | La baie de services est-elle également utilisée pour faire du lavage auto ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | J.07 | Is the station connected to the public wastewater network (sewers)? | La station dispose-t-elle d'un raccordement au réseau public d'eaux usées (égouts) ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Les portiques et autres équipements mobiles de lavage sont-ils tous correctement positionnés pour éviter tout risque d'écrasement en fonctionnement ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 08 Nov 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 08 Nov 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Prévoir la mise en conformité des installations photovoltaïques pour être conforme à l'invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Ces limiteurs disposent-ils de systèmes de vérifications périodiques de bon fonctionnement ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Chebika | TN111S2223 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 08 Feb 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Y a-t-il des équipements électriques (ex: moteur, pompe) placés à proximité d'une source d'eau ? | N |  | 21 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | E.11a | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | Si "NON", un périmètre de sécurité de 5m autours du dépotage doit être mis en place, avec neutralisation temporaire des îlots adjacents. Le personnel du site est-il au courant ? | N |  | 21 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur en place par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 3m d'un ouverture, d'un point électrique, d'un point bas, de la limite de propriété du site ou la voie publique ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | G.15 | Is there at least one ABC powder extinguisher in the bay? | A-t-on bien au moins un extincteurs à poudre ABC dans la baie ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Prévoir la mise en conformité des installations photovoltaïques pour être conforme à l'invariant ES04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Prévoir la mise à jour des plans électriques du site en incluant les installation PV. | N |  | 21 Jan 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Mettre en conformité la distance des évents pour se conformer à l'invariant EP09. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | F.02f | Are all gas cylinders (full and empty) more than 5m from the site's hydrocarbon tanks or dispensing equipment? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 5m des cuves hydrocarbures ou appareils distributeurs du site ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | J.01 | Does the station have a fire blanket? | Prévoir la mise en place d'une couverture antifeu sur la station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | N |  | 21 Jul 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Si la station a une boutique, celle-ci est-elle équipée de douches et de vestiaires pour le personnel ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Medjez El Bab | TN111S2240 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Fournir un schéma des installations électriques à jour à la station. | N |  | 26 Jun 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Prévoir l'installation d'un report d'arrêt d'urgence dédié à la piste et accessible instantanément par le personnel de la station. | N |  | 26 Jun 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | E.06 | Are all the offloading coupling ports padlocked? | Les bouches de dépotage sont-elles toutes bien cadenassées ? | N |  | 26 Jun 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | E.12b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié à l'entretien des séparateurs hydrocarbures. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | A.11b | If “YES”, is there a specific procedure for intervening near these power lines, and is it known by the station staff? | Si "OUI", une procédure spécifique d'intervention à proximité de ces lignes électriques existe-t-elle, et est-elle connu de l'exploitant du site ? | N |  | 26 Jun 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Prévoir la mise en place d'un extincteur ABC à proximité immédiate du groupe électrogène. | N |  | 26 Jun 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | B.08 | Is there any electrical equipment (e.g. motor or pump) close to a water souce? | Y a-t-il des équipements électriques (ex: moteur, pompe) placés à proximité d'une source d'eau ? | N |  | 26 Jun 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | B.09 | Is there a CO2 extinguisher specifically for electrical fires near each station's electrical box? | Prévoir la mise en place d'un extincteur CO2 dédié aux feux d'origine électrique à proximité de chaque coffret électriques du site. | N |  | 26 Jun 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET01. | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | E.11a | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | Si "NON", un périmètre de sécurité de 5m autours du dépotage doit être mis en place, avec neutralisation temporaire des îlots adjacents. Le personnel du site est-il au courant ? | N |  | 26 Jun 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | G.07 | Is the service bay also used for car washing? | La baie de services est-elle également utilisée pour faire du lavage auto ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | D.06 | Are all the station's fuel tanks double-walled? | Toutes les cuves carburants de la station sont-elles bien double-enveloppe ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | G.03 | Is the service bay equipped with “no smoking” signs? | Prévoir la mise en place de panneaux "interdiction de fumer" dans la baie. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Prévoir la mise en place de têtes de jauge type "baïonnette" sur site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Prévoir une remise en état des cheminée pour se conformer à l'invariant EP04. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | La station a-t-elle des cuves simple-enveloppe enfouies ou en fosse maçonnée ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | F.02h | Are all gas cylinders (full and empty) more than 3m from an opening, an electrical point, a low point, the site property limits? | Toutes les bouteilles de gaz (pleines et vides) sont-elles à plus de 3m d'un ouverture, d'un point électrique, d'un point bas, de la limite de propriété du site ou la voie publique ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Prévoir la mise en place d'un contrat de maintenance dédié aux séparateurs. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Les comptes-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Le personnel de la station connaît-il et dispose-t-il du Manuel Station (edition 2024) ? | N |  | 26 Jun 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Prévoir la mise en place du "Réagir en Cas d'Urgence" sur site. | N |  | 26 Jun 2025
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Prévoir la mise en place d'un accroche échelle sur l'auvent de la station. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | G.16 | Are the fire extinguishers in the bay sealed? | Les extincteurs de la baie sont-ils plombés ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | G.17 | Is the date of the last fire extinguisher inspection less than 1 year old? | La date du dernier contrôle des extincteurs est-elle inférieure à 1 an? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Prévoir la mise en place d'un accroche-échelle ou d'un échelle à crinoline sur le bâtiment du site. | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | D.20b | Have these single-walled tanks been coated/stratified? | Ces cuves simple-enveloppe ont-elles été stratifiées? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | La fosse maçonnée dispose-t-elle d'un regard de visite permettant de contrôler l'état à l'intérieur de la fosse ? | N |  | 31 Dec 2030
AFR | MOI | TotalEnergies Marketing Tunisie | Sidi Hassine | TN111S2221 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 12 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 12 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 12 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 12 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 12 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.02 | Are the bay and its storage area clean, with a non-slip floor? | Are the bay and its storage area clean, with a non-slip floor? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 12 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 12 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 12 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 12 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 12 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 12 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Aba Ctr | NG111S0149 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Abakaliki | NG111S0168 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 16 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Abakaliki | NG111S0168 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton relay dedicated to forecourt and instantly accessible by station staff. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Abakaliki | NG111S0168 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Abakaliki | NG111S0168 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Abakaliki | NG111S0168 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Abakaliki | NG111S0168 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 16 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Abakaliki | NG111S0168 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Abakaliki | NG111S0168 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading area into compliance with the Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Abakaliki | NG111S0168 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Abakaliki | NG111S0168 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 18 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 18 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 18 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 18 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 18 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 18 Dec 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Addoh Road | NG111S0423 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 17 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 17 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 17 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | C.15a | If "YES", is the site equipped with an emergency call system connected to a remote monitoring center or to a person designated and trained to handle incidents? | Plan to comply with invariant ES08 on unsupervised forecourt. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.04c | If "NO", are there anti-siphon valves on the suction pipes of above-ground tanks? | Install anti-siphon valves on above-ground tank pipes. | N |  | 17 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.37 | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 17 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Does the station have showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 17 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | K.19 | Is the station equipped with batteries? | Is the PV system equipped with batteries? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 17 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 17 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ademulegun Rd | NG111S0208 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Are PV installations equipped with visible, regulation-compliant safety signs? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton relay dedicated to forecourt and instantly accessible by station staff. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading area into compliance with the Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop to comply with Invariant ES05. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor | NG111S0217 | E.03 | Is the offloading area oil-tight? | Plan to make the offloading area compliant with Invariant ET04. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | B.07 | Are equipment and protections of electrical installations designed to allow electrical lockout/tagout? | Plan work to bring the site's electrical protection into line with invariant ES06 on lockout/tagout. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | B.16 | Does the station have a general emergency stop button ? | Install a general emergency stop button for the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker upstream of electrical installations. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Agbor Express | NG111S0622 | E.03 | Is the offloading area oil-tight? | Plan to make the offloading area compliant with Invariant ET04. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 22 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 22 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 22 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 22 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 22 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 22 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | K.07 | Do photovoltaic systems have a dedicated emergency stop button? | Plan to install a dedicated solar emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 22 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 22 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akoka | NG111S0036 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 22 Jan 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 21 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 21 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 21 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 21 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 21 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 21 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 21 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 21 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Are PV installations equipped with visible, regulation-compliant safety signs? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.37 | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 21 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | K.19 | Is the station equipped with batteries? | Is the PV system equipped with batteries? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 21 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Akure Motor Park | NG111S0209 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Alausa | NG111S0060 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Alausa | NG111S0060 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Alausa | NG111S0060 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Alausa | NG111S0060 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Alausa | NG111S0060 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 03 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Alausa | NG111S0060 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Alausa | NG111S0060 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Alausa | NG111S0060 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 19 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | E.03 | Is the offloading area oil-tight? | Plan to make the offloading area compliant with Invariant ET04. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Coker | NG111S0612 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Plan to bring the bay's water treatment back into compliance with Invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 19 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | E.03 | Is the offloading area oil-tight? | Plan to make the offloading area compliant with Invariant ET04. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Ferry | NG111S0218 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Plan to bring the bay's water treatment back into compliance with Invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton relay dedicated to forecourt and instantly accessible by station staff. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters to collect water from the forecourt and send it to a separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tank compartments on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop to comply with Invariant ES05. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | D.06 | Are all the station's fuel tanks double-walled? | Plan for the replacement of the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | E.03 | Is the offloading area oil-tight? | Plan to make the offloading area compliant with Invariant ET04. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Asaba Umuezei | NG111S0219 | J.07 | Is the station connected to the public wastewater network (sewers)? | Ensure that the site's wastewater complies with Invariant ET03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton relay dedicated to forecourt and instantly accessible by station staff. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Plan to install a wastewater treatment system in accordance with invariant ET03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker upstream of electrical installations. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 19 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Connect the offloading couplings to the site's grounding system in a visible manner, in accordance with Invariant ES02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bayelsa | NG111S0636 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Plan to bring the bay's water treatment back into compliance with Invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 19 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benin/Asaba Exp | NG111S0451 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | Plan a structural study in accordance with the recommendations of Invariants ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benson Bus Stop | NG111S0388 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benson Bus Stop | NG111S0388 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Benson Bus Stop | NG111S0388 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 19 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head 2 Osadebe | NG111S0222 | E.03 | Is the offloading area oil-tight? | Plan to make the offloading area compliant with Invariant ET04. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | C.05 | Is the station's forecourt area oil-tight? | Prévoir la remise en état de la dalle de distribution pour être conforme à l'invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Prévoir l'installation d'une téléjauge sur la station. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Prévoir le remplacement des tuyauteries non-PEHD pour être conforme à l'invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Prévoir le remplacement des tuyauteries de dépotage pour les passer en double-enveloppe et être conforme à l'EP06 | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets en pied de volucompteur type RISBRIDGER. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Prévoir le pré-équipement RV1 du site pour être conforme à l'EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Prévoir la mise en place de raccords cassants sur l'ensembles des flexibles du sites. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipements de baie. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Prévoir la mise en conformité des installations photovoltaïques pour être conforme à l'invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | D.23 | Is there a compliant pipe integrity test report available for this station? | Prévoir la réalisation d'une réépreuve acoustique des installations pétrolières du site. | N |  | 19 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Prévoir une remise en conformité des dépotages selon l'Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | E.03 | Is the offloading area oil-tight? | Prévoir une remise en conformité des dépotages selon l'Invariant ET04. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Prévoir une remise en conformité du traitement des eaux de la baie selon l'Invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bridge Head Asaba | NG111S0223 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | Prévoir une étude de structure selon les préconisations de l'Invariants ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bukuru Bye Pass | NG111S0318 | D.16 | Does the station have a graduated gauge ruler in good condition, allowing manual gauging to be carried out? | Provide a gauging ruler to the station. | N |  | 29 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bukuru Bye Pass | NG111S0318 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bukuru Bye Pass | NG111S0318 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bukuru Bye Pass | NG111S0318 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 29 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bukuru Bye Pass | NG111S0318 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bukuru Bye Pass | NG111S0318 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bukuru Bye Pass | NG111S0318 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 29 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bukuru Bye Pass | NG111S0318 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 29 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bukuru Bye Pass | NG111S0318 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 29 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bukuru Bye Pass | NG111S0318 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Bukuru Bye Pass | NG111S0318 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 15 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 15 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 15 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 15 Jan 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 15 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Coronation | NG111S0347 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Doka Crs | NG111S0307 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Doka Crs | NG111S0307 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Doka Crs | NG111S0307 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Doka Crs | NG111S0307 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 04 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Doka Crs | NG111S0307 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 04 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Doka Crs | NG111S0307 | B.13c | Is there a CO2 extinguisher next to the generator electrical panel? | Install an CO2 fire extinguisher in the immediate vicinity of the generator electrical panel. | N |  | 04 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Doka Crs | NG111S0307 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Doka Crs | NG111S0307 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Doka Crs | NG111S0307 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Doka Crs | NG111S0307 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Doka Crs | NG111S0307 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 04 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 14 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | G.02 | Are the bay and its storage area clean, with a non-slip floor? | Are the bay and its storage area clean, with a non-slip floor? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 14 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 14 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Egbeda | NG111S1068 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 14 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton relay dedicated to forecourt and instantly accessible by station staff. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Plan to install a wastewater treatment system in accordance with invariant ET03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading area into compliance with the Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop to comply with Invariant ES05. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 19 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Elele Alimini - | NG111S0197 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Plan to bring the bay's water treatment back into compliance with Invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Garage | NG111S0027 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 02 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Garage | NG111S0027 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Garage | NG111S0027 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Garage | NG111S0027 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Garage | NG111S0027 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Garage | NG111S0027 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 02 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Garage | NG111S0027 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Garage | NG111S0027 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Garage | NG111S0027 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 02 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Garage | NG111S0027 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 25 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 25 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 25 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 25 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 25 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Epe Town | NG111S0047 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 22 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 22 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 22 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 22 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.37 | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 22 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 22 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 22 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Does the station have showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 22 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 22 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 22 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Erekesan Market | NG111S0210 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 15 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 15 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | H.04 | Is the lighting of washing areas sufficient and operational? | Plan to revamp the lighting in the carwash area. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Farm Center | NG111S0835 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 04 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | H.04 | Is the lighting of washing areas sufficient and operational? | Plan to revamp the lighting in the carwash area. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | K.10 | Is there a type 1+2 DC lightning and surge arrester on the PV system? | Is there lightning conductor (surger protector) DC type 1+2 (combined lighting protection and surge protection) ? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | K.19 | Is the station equipped with batteries? | Is the PV system equipped with batteries? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 04 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 04 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | K.02 | Are the photovoltaic systems located on the canopy or a shading roof? | Are the photovoltaic systems located on the canopy or a shading roof? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | K.09 | Is there a DC breaking device between the inverter and the PV modules? | Is there a breaking device (DC current) between the inverter and the PV modules (it may be integrated into the inverter)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 04 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gboko (Market Road) | NG111S0294 | D.37 | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 18 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tank compartments on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 18 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop to comply with Invariant ES05. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | K.07 | Do photovoltaic systems have a dedicated emergency stop button? | Plan to install a dedicated solar emergency stop to comply with Invariant ES05. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | K.09 | Is there a DC breaking device between the inverter and the PV modules? | Bring photovoltaic electrical installations into compliance with the technical specifications of Invariant ES05. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | K.11 | Is there a 300mA differential circuit breaker upstream of the PV system? | Install a 300mA earth leakage circuit breaker for the PV system. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | K.12 | Is there a Type 2 surge protection device in the PV system's AC cabinet? | Plan to install a Type 2 surge protection device in the AC part of the PV system. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 18 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | K.15 | Are PV inverters installed in a place that is inaccessible to the public, and protected from rain and UV rays? | Protect and secure the site's photovoltaic installations. | N |  | 18 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 18 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | K.10 | Is there a type 1+2 DC lightning and surge arrester on the PV system? | Bring photovoltaic electrical installations into compliance with the technical specifications of Invariant ES05. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gra | NG111S0199 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | Plan a structural study in accordance with the recommendations of Invariants ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Gwarzo Road 2 Jang | NG111S0619 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Hotoro Road | NG111S0349 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 19 Dec 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 29 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 29 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Does the station have showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 29 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Idah | NG111S1002 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 03 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 03 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 03 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 03 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 03 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Rd | NG111S0041 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Town | NG111S0019 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Town | NG111S0019 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ikorodu Town | NG111S0019 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 18 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 18 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 18 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 18 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 18 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 18 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 18 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ilesha Road | NG111S0211 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ipara | NG111S0020 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 14 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ipara | NG111S0020 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ipara | NG111S0020 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ipara | NG111S0020 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install Class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ipara | NG111S0020 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ipara | NG111S0020 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iperu | NG111S0031 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iperu | NG111S0031 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tank compartments on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iperu | NG111S0031 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iperu | NG111S0031 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iperu | NG111S0031 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iperu | NG111S0031 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iperu | NG111S0031 | D.06 | Are all the station's fuel tanks double-walled? | Plan for the replacement of the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iperu | NG111S0031 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 19 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ishara | NG111S0021 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ishara | NG111S0021 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ishara | NG111S0021 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ishara | NG111S0021 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ishara | NG111S0021 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ishara | NG111S0021 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ishara | NG111S0021 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 16 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 17 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 17 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | K.05 | Is the access to photovoltaic installations at height done via a ladder-hook or a caged ladder? | Bring photovoltaic installations into compliance with invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo M/P | NG111S0143 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 17 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 08 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Provide concrete blocks on islands to protect dispensers from crashes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 08 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 08 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 08 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iwo Road | NG111S0111 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 08 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iyana Meiran | NG111S0550 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iyana Meiran | NG111S0550 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iyana Meiran | NG111S0550 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iyana Meiran | NG111S0550 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iyana Meiran | NG111S0550 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Iyana Meiran | NG111S0550 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 19 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | B.12 | Are the electrical conduits coming from the forecourt into the building properly sealed? | Ensure that electrical conduits are sealed off to avoid vapour problems. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | C.06 | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | Is the dispenser base clean, with no visible fuel leaks on the dispenser islands? | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 26 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 26 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 26 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jama'are | NG111S0350 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 13 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 13 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 13 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 13 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Jubilee Estate | NG111S0857 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 13 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 16 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 16 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 16 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Does the station have showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 16 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kaduna Road Kontagora | NG111S0275 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 15 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 15 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 15 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is there a compliant pipe integrity test report available for this station? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 15 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 15 Jan 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | H.04 | Is the lighting of washing areas sufficient and operational? | Plan to revamp the lighting in the carwash area. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 15 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kano Co-Op | NG111S0360 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Katsina Road | NG111S0361 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 19 Dec 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 07 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 07 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 07 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 07 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km 40 | NG111S0392 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 05 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Plan for a revamping of the offloading area. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | E.11a | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | If “NO”, a 5m safety perimeter around the offloading must be set up, with temporary neutralization of adjacent islands. Are site station staff aware of this process? | N |  | 05 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | J.01 | Does the station have a fire blanket? | Plan to install a fire blanket on the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 05 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | J.03 | Does the station have a first-aid kit? | Does the station have a first-aid kit? | N |  | 05 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | J.08 | Are food products stored separately from non-food products? | Are food products stored separately from non-food products? | N |  | 05 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 05 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Plan to install a wastewater treatment system in accordance with invariant ET03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Km2 | NG111S0420 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 05 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 07 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.02a | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 07 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 automatic gauge on the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.02d | Is there a maintenance contract dedicated to pressurized installations with submersible pumps ? | Plan to set up a maintenance contract dedicated to pressuried sites equipped with STPs. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.02e | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.10 | Are the road covers for manhole chimneys heavy and difficult to handle? With the risk of unintentional closure? | Plan to replace road covers by composite equipment. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | H.01 | Is the flooring of the carwash areas non-slippery? | Is the flooring of the carwash areas non-slippery? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 07 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.02n | Are there shear valves, firmly fixed to the dispensing islands, at the feet of all dispensers? | Install breakaway shear valves at the feet of all dispensers. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.02p | Are prefabricated PE oiltight sumps installed below all dispensers on the pressurized site ? | Plan to install prefabricated PE oiltight sumps below all dispensers on the pressurized site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 07 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Install PLLD (Pressurized Line Leak Detector) pressure sensors on all submersible pumps on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.02l | Is the automatic gauging system interconnected to the dispensers to enable stock reconciliation and continuous leak detection? | Plan to install the dedicated management module in the automatic gauge. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Is there a forced-running mode for submersible pumps, known and available to station staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kuje | NG111S0963 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 07 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 30 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 30 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 30 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | K.13 | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | As part of the station solarization, has a structural study been carried out for each structure receiving PV modules? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 31 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Kurudu | NG111S0304 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 31 Oct 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | D.16 | Does the station have a graduated gauge ruler in good condition, allowing manual gauging to be carried out? | Provide a gauging ruler to the station. | N |  | 10 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 10 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | D.18 | Does the station staff carry out a daily check of fuel stocks, reconciling physical and accounting inventories? | Does the station staff carry out a daily check of fuel stocks, reconciling physical and accounting inventories? | N |  | 10 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | D.19 | Does the station manager monitor fuel losses: WetStock Management? | Does the station manager monitor fuel losses: WetStock Management? | N |  | 10 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 10 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Lagos Road Kontagora | NG111S0276 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mamu | NG111S0032 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Masaka 2 | NG111S0266 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Masaka 2 | NG111S0266 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Masaka 2 | NG111S0266 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Masaka 2 | NG111S0266 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Masaka 2 | NG111S0266 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Masaka 2 | NG111S0266 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Masaka 2 | NG111S0266 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Masaka 2 | NG111S0266 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Masaka 2 | NG111S0266 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Masaka 2 | NG111S0266 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 28 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Masaka 2 | NG111S0266 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 28 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 25 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 25 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | C.14 | Is station lighting sufficient and operational ? | Plan to revamp the station's lighting. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 25 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0056 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 18 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 18 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | D.26 | Are vent heads at least 4m high from the ground? | Raise vent heads to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading area into compliance with the Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 18 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 18 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 2 | NG111S0201 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 5 | NG111S0202 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 16 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 5 | NG111S0202 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters to collect water from the forecourt and send it to a separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 5 | NG111S0202 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 5 | NG111S0202 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tank compartments on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 5 | NG111S0202 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 5 | NG111S0202 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 16 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 5 | NG111S0202 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 16 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 5 | NG111S0202 | D.29 | Are the vents more than 5 meters from the station's dispensers ? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 5 | NG111S0202 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mile 5 | NG111S0202 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton dedicated to the forecourt and instantly accessible by station staff. | N |  | 27 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 27 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 27 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mission Hill | NG111S0461 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 28 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 28 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 28 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker at the top of the electrical panel. | N |  | 28 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 28 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 28 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 28 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mkd Centre | NG111S0298 | D.37 | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 20 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 20 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton dedicated to the forecourt and instantly accessible by station staff. | N |  | 20 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 20 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Mokwa | NG111S0277 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Plan to install a wastewater treatment system in accordance with invariant ET03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 13 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | B.03 | Is the station's electrical panel equipped with a 300mA differential circuit breaker? | Plan to install a 300mA differential circuit breaker upstream of electrical installations. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.11 | Are the gauge heads hermetically sealed to prevent vapors into the manhole chimney? | Plan to install a “bayonet” type gauge heads on site. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.16 | Does the station have a graduated gauge ruler in good condition, allowing manual gauging to be carried out? | Provide a gauging ruler to the station. | N |  | 13 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.28 | Are the vents more than 3 meters from an electrical source? | Adjust vent distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.30 | Are the vents visible to the truck driver/deliverer from the offloading area during tank filling operations? | Adjust vent distance to make them visible from the offloading and comply with invariant EP09. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.31 | Are the vents visibly connected to the station's earthing / grounding network? | Make a visible earth connection to the vents. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | E.03 | Is the offloading area oil-tight? | Plan to make the offloading area compliant with Invariant ET04. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Plan to bring offloading area into compliance with invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Numan Ferry | NG111S0377 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Connect the offloading couplings to the site's grounding system in a visible manner, in accordance with Invariant ES02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Obajana | NG111S0807 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Obajana | NG111S0807 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Obajana | NG111S0807 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Obajana | NG111S0807 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ode Remo | NG111S0421 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ode Remo | NG111S0421 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ode Remo | NG111S0421 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ode Remo | NG111S0421 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ode Remo | NG111S0421 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ode Remo | NG111S0421 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 19 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Prévoir la réalisation de l'étanchéité sous les appareils distributeurs selon l'invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Mettre en place ou remplacer les clapets existants par des clapets RISBRIDGER. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Prévoir l'installation de sondes de détection carburants dans les cheminées trou-d'homme. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Faire retirer les autres clapets pour éviter la rétention de produit dans les tuyauteries. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | La station dispose-t-elle d'un carnet de Plans de Prévention Journalier pour les interventions de contractants extérieures ? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Prévoir le remplacement du séparateur existant par un équipement conforme à l'invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Les compte-rendus des visites d'entretien et de nettoyage du séparateur sont-ils disponibles sur site ? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Prévoir le déplacement des équipements mobiles pour éviter les risques d'écrasement. | N |  | 26 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | La baie de service est-elle équipée d'une cage de sécurité correctement dimensionnée pour le gonflage de tous les types de pneus ? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Prévoir la réalisation des contrôles réglementaires des équipement de baie. | N |  | 26 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Les autres déchets de la baie sont-ils triés entre déchets dangereux et non dangereux ? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | G.24 | Are used tires collected and processed appropriately? | Les pneus usagés sont-ils collectés et traités de manière appropriée ? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | G.18 | Are used oils stored in a double-walled tank? | Les huiles usée sont-elles stockées dans une cuve enterrée double-enveloppe ? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | G.19 | Is the used oil tank equipped with a retention basin? | Les huiles usée sont-elles stockées dans une cuve aérienne avec cuvette de rétention ? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | G.22 | Are used batteries collected and properly treated? | Les batteries usagées sont-elles collectées et traitées de manière appropriée ? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogbor Hill | NG111S0154 | G.20 | Is used oil collected and properly treated? | Les huiles usées sont-elles collectées et traitées correctement ? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogijo | NG111S0022 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogijo | NG111S0022 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogijo | NG111S0022 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ogijo | NG111S0022 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 13 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Provide concrete blocks on islands to protect dispensers from crashes. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.02b | Does the affiliate have a specific system for monitoring, justifying and tracing fuel losses at service stations in writing?" | Set up a specific organization to monitor fuel losses at filling stations. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.02d | Is there a maintenance contract dedicated to pressurized installations with submersible pumps ? | Plan to set up a maintenance contract dedicated to pressuried sites equipped with STPs. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.02g | Are the maintenance contractors working on the pressurized systems specifically qualified to maintain this type of installation? | Contact your submersible pump supplier to arrange training for local contractors. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 or DOVER PROGAUGE ATG on the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Install PLLD (Pressurized Line Leak Detector) pressure sensors on all submersible pumps on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.02l | Is the automatic gauging system interconnected to the dispensers to enable stock reconciliation and continuous leak detection? | Plan to install the dedicated management module in the automatic gauge. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.02n | Are there shear valves, firmly fixed to the dispensing islands, at the feet of all dispensers? | Install breakaway shear valves at the feet of all dispensers. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.02p | Are prefabricated PE oiltight sumps installed below all dispensers on the pressurized site ? | Plan to install prefabricated PE oiltight sumps below all dispensers on the pressurized site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.26 | Are vent heads at least 4m high from the ground? | Raise vent heads to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.27 | Is the base of the vents more than 5m from the building's openings and from a low point such as a gutter? | Adjust vents distance to comply with invariant EP09. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Plan for renovation of the offloading area in line with invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Implement the LockOut - TagOut procedures for the maintenance of pressurized sites and inform the station staff. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Plan to upgrade the fuel pipes to comply with the EP11 invariant compensatory measure. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | D.23 | Is there a compliant pipe integrity test report available for this station? | Plan to carry out an integrity acoustic test of the site's petroleum installations. | N |  | 13 May 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | E.03 | Is the offloading area oil-tight? | Plan to make the offloading area compliant with Invariant ET04. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oji River | NG111S0173 | E.09 | Are the offloading couplings visibly connected to the station's grounding network using a copper cable with a minimum cross-section of 16 mm2? | Connect the offloading couplings to the site's grounding system in a visible manner, in accordance with Invariant ES02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 13 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | E.03 | Is the offloading area oil-tight? | Plan to make the offloading area compliant with Invariant ET04. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oke Odo | NG111S0015 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Plan to bring the bay's water treatment back into compliance with Invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | E.04 | Are offloading couplings above ground, or less than 30 cm below forecourt level? | Plan for a revamping of the offloading area. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | C.11b | Do all the sand boxes have a lid / cover? | Do all the sand boxes have a lid / cover? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | C.11c | Is the sand clean and free of waste in all sandboxes | Is the sand clean and free of waste in all sandboxes | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | C.11a | Is there a shovel in every sandbox? | Is there a shovel in every sandbox? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02d | Is there a maintenance contract dedicated to pressurized installations with submersible pumps ? | Plan to set up a maintenance contract dedicated to pressuried sites equipped with STPs. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02e | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | Does this maintenance contract provide for a 24-hour back-up of pressurized installations if necessary? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02f | Does the affiliate use a ticketing tool to track maintenance operations and fault resolution times? | Does the affiliate use a ticketing tool to track maintenance operations and fault resolution times? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02a | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | Has the affiliate obtained a validated waiver for pressurized sites with STPs in POLARION? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02b | Does the affiliate have a specific system for monitoring, justifying and tracing fuel losses at service stations in writing?" | Set up a specific organization to monitor fuel losses at filling stations. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02g | Are the maintenance contractors working on the pressurized systems specifically qualified to maintain this type of installation? | Contact your submersible pump supplier to arrange training for local contractors. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02j | Are all the submersible pumps in the pressurized installation fitted with PLLD (Pressurized Line Leak Detector) pressure sensors? | Install PLLD (Pressurized Line Leak Detector) pressure sensors on all submersible pumps on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02k | Are all the submersible pumps in the pressurized installation connected to an STP control box (Submersible Turbine Pumps)? | Plan to install STP control boxes. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02l | Is the automatic gauging system interconnected to the dispensers to enable stock reconciliation and continuous leak detection? | Plan to install the dedicated management module in the automatic gauge. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02m | Are ALL pressurized pipes made of double-walled HDPE (and not just the offloading pipes)? | Are all the gas station pipes made of double-walled HDPE (and not just the offloading pipes)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02r | Are there Specific LockOut - TagOut procedures for maintenance of pressurized sites equipped with STPs, known by station staff? | Is there a forced-running mode for submersible pumps, known and available to station staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02h | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | Has a process been drawn up and approved by the maintenance contractor indicating the obligation to recheck pipings tightness after a disconnection? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02i | Is the station equipped with an Automatic Gauging System with a dedicated management module for submersible pump pressure sensors? | Plan to install a GILBARCO TLS 350/450 automatic gauge on the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02o | Are the pressurized pipes more than 15 years old? | Are the pressurized pipes more than 15 years old? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02p | Are prefabricated PE oiltight sumps installed below all dispensers on the pressurized site ? | Plan to install prefabricated PE oiltight sumps below all dispensers on the pressurized site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.02q | Have the station staff been trained to the specific features of pressurized sites with STPs ? | Train station staff to the specific features of pressurized sites with STPs. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Okigwe | NG111S0155 | D.35 | Are dispenser hoses in good condition and less than 6 years old ? | Replace old hoses or hoses more than 6 years old. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 27 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 27 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 27 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.02 | Are the bay and its storage area clean, with a non-slip floor? | Are the bay and its storage area clean, with a non-slip floor? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | C.13 | Are dispensers protected from shocks by concrete protection blocks on the forecourt islands ? | Provide concrete blocks on islands to protect dispensers from crashes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 27 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 27 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 27 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Aba Rd Umuahia | NG111S0156 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 10 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 10 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 10 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Old Sec Rd Asaba | NG111S0462 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 22 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | J.07 | Is the station connected to the public wastewater network (sewers)? | Is the station connected to the public wastewater network (sewers)? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 22 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 22 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 22 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 22 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.20 | Does the station have single-walled tanks buried in the ground or in a concrete pit? | Does the station have single-walled tanks buried in the ground or in a concrete pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.37 | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | Can you tell us whether warning mesh were installed on buried cables and pipes during the latest reconstruction work on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 22 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Does the station have showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 22 Jan 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 22 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 22 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Motor Park | NG111S0212 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 05 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 05 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 05 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 05 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 05 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 05 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 05 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 05 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ondo Rd | NG111S0870 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Opp Govt Coll | NG111S0389 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Opp Govt Coll | NG111S0389 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Opp Govt Coll | NG111S0389 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 11 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | B.06 | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | Are electrical installations in satisfactory general condition (age, wiring, temporary installations, condition of circuit breakers)? | N |  | 11 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 11 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 11 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Oshodi | NG111S0071 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ota Ona | NG111S1062 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Otukpo Rd | NG111S0300 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Otukpo Rd | NG111S0300 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Otukpo Rd | NG111S0300 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Otukpo Rd | NG111S0300 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Otukpo Rd | NG111S0300 | C.15a | If "YES", is the site equipped with an emergency call system connected to a remote monitoring center or to a person designated and trained to handle incidents? | Plan to comply with invariant ES08 on unsupervised forecourt. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Otukpo Rd | NG111S0300 | D.05a | Do these overfill protection devices have systems for periodic verification of proper operation? | Are the overfill protection devices tested regularly? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 27 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | B.14 | Is the installation equipped with at least one 30mA defferential circuit breaker for direct-contact equipment (such as sockets)? | Install 30 mA differential circuit breakers to comply with invariant ES07. | N |  | 27 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | E.10 | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | Is the offloading area equipped with a grounding system to connect the delivery truck: spike / clamp / reel? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 27 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | E.07 | Is the offloading area correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone/ COV1 / Separator? | Plan to completely upgrade the offloading signage. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Does the station have showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 27 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Centre | NG111S0248 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | E.03 | Is the offloading area oil-tight? | Is the offloading area oil-tight and anti-slip? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | Does the station have showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 26 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 26 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | K.07 | Do photovoltaic systems have a dedicated emergency stop button? | Plan to install a dedicated solar emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 26 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Owo Road | NG111S0235 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton relay dedicated to forecourt and instantly accessible by station staff. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | J.07a | If “NO”, does the station have a wastewater treatment system: septic tank / all-water tank / wastewater treatment plant? | Plan to install a wastewater treatment system in accordance with invariant ET03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | D.08 | Are all tank compartments correctly identified with a standardized metal plate: color / product / #tank / #compartment / capacity? | Plan to revamp product signage on tanks. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading area into compliance with the Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop to comply with Invariant ES05. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | D.33 | Are flame arresters (RIDART type) present at the unleaded vent heads? | Plan to install flame arresters (RIDART type) on unleaded vent heads? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Palm Expressway | NG111S0940 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Plan to bring the bay's water treatment back into compliance with Invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | B.13b | Is there an ABC fire extinguisher in the immediate vicinity of the generator? | Install an ABC fire extinguisher in the immediate vicinity of the generator. | N |  | 16 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | J.10 | Is the “React in an Emergency” binder available on site, completed with emergency numbers, and positioned close to the cashier desk and pump attendants? | Provide “React in an Emergency” document on the station. | N |  | 16 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 16 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 16 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 16 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 1 | NG111S0204 | G.15 | Is there at least one ABC powder extinguisher in the bay? | Install fire extinguishers in the bay to comply with Invariants ES01. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | B.04 | Are electrical installations properly labelled using printed labels or engraved plates? | Plan to refurbish the station's electrical panel signage. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | E.12c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 26 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | H.01 | Is the flooring of the carwash areas non-slippery? | Is the flooring of the carwash areas non-slippery? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 26 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 26 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ph 2 | NG111S0205 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 26 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sagamu Junction | NG111S0390 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sagamu Junction | NG111S0390 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sagamu Junction | NG111S0390 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sagamu Lagos Road | NG111S0024 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sagamu Lagos Road | NG111S0024 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sagamu Lagos Road | NG111S0024 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sagamu Lagos Road | NG111S0024 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sango | NG111S0118 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sango | NG111S0118 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sango | NG111S0118 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sango | NG111S0118 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sango | NG111S0118 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 22 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sango | NG111S0118 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Sango | NG111S0118 | J.06 | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | Are station staff aware of ticketing process for maintenance interventions in the event of equipment breakdown on site (DAISY WorldWide)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 27 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tegina | NG111S0280 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 09 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 09 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | E.08 | Are the offloading couplings protected against collision with concrete blocks or bollards? | Are the offloading couplings protected against collision with concrete blocks or bollards? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | J.09 | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | Are station employees properly equipped with the required PPE: high visibility vest + helmet + safety shoes + gloves + glasses? | N |  | 09 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tinubu Village | NG111S0044 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 09 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Toyin St | NG111S0427 | E.06 | Are all the offloading coupling ports padlocked? | Are all the offloading coupling ports padlocked? | N |  | 22 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Toyin St | NG111S0427 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Toyin St | NG111S0427 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Toyin St | NG111S0427 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Toyin St | NG111S0427 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 22 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Toyin St | NG111S0427 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 22 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Toyin St | NG111S0427 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Toyin St | NG111S0427 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Toyin St | NG111S0427 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Toyin St | NG111S0427 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 20 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 20 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | J.18a | If “YES”, are all the site's canopies equipped with a permanent and operational ladder-kook? | Plan to install a ladder hook on the station canopy. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 20 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Tundun Fulani | NG111S0281 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 26 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 26 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Ukwa Town | NG111S0863 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | E.02 | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | Can the fuel delivery truck leave the offloading area in forward gear, without having to maneuver? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.04 | If the bay is equipped with one or more pits, are they equipped with guardrail wheel tracks? | Install guardrail wheel tracks to secure pits in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | E.05 | Are offloading couplings grouped together in the same place, in accordance with the AMETHYST guidelines? | Plan to bring offloading couplings into compliance with the EP10 invariant. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.05 | Is the pits and bay drainage system operational and in good condition? | Is the pits and bay drainage system operational and in good condition? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 24 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | D.06a | Are these double-walled tanks equipped with leak detectors? | Plan to install class 2 leak detectors on all double-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 24 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 24 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umuahia | NG111S0955 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | B.16a | Is there a dedicated emergency stop for the forecourt power supply, present at the cashier desk (or on the forecourt) and instantly accessible to station staff personnel? | Install an emergency stop botton relay dedicated to forecourt and instantly accessible by station staff. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | B.17 | Is there an electrical inspection report on the station, less than a year old? | Have a full inspection of the site's electrical installations carried out by an approved inspection body. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | J.19a | If “YES”, are all the station's buildings equipped with at least one ladder-hook or a caged ladder? | Arrange for a ladder-hook or a caged ladder to be installed on the site building to comply with Invariant ES04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | C.05 | Is the station's forecourt area oil-tight? | Plan to upgrade the forecourt concrete slab to comply with invariant ET05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.07 | Are the tanks linked to the earthing / grounding network of the station? | Plan to connect all tanks to the grounding network of the station. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.12 | Are the manhole chimneys / sumps above tanks oil and vapor tight? | Plan to revamp sumps above tanks to comply with invariant EP04. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes to comply with invariant EP06. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER type valves at the foot of dispensers. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.32 | Are all site vents correctly identified with standardized signage: color / product / #tank / #compartment / capacity / no-smoking / no phone / ATEX Zone ? | Plan a complete upgrade of vents signage. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.36 | Are all dispensers hoses equipped with breakaway couplings? | Plan to install breakaway couplings on all station hoses. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | K.08 | Is the forecourt emergency stop properly coupled to the photovoltaic system, so that it disconnects if activated? | Plan to connect PV systems to the station's forecourt emergency stop to comply with Invariant ES05. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | K.23 | Is the safety signage dedicated to the presence of batteries present and in good condition: electrical hazard / no smoking / risk of explosion? | Plan to bring signage on the site's battery installations into compliance. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 19 Nov 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | D.06 | Are all the station's fuel tanks double-walled? | Plan for the replacement of the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Plan to make the offloading area compliant with Invariant EP10. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Umunede | NG111S0225 | E.03 | Is the offloading area oil-tight? | Plan to make the offloading area compliant with Invariant ET04. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | G.06 | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | If the bay is equipped with pits, are they secured with a safety galvanized gratings? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | G.07 | Is the service bay also used for car washing? | Is the service bay also used for car washing? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 21 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | C.09b | If "YES", is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | C.09c | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | D.16 | Does the station have a graduated gauge ruler in good condition, allowing manual gauging to be carried out? | Provide a gauging ruler to the station. | N |  | 21 Apr 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Utako (Em World) | NG111S0962 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 21 Jul 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Ave | NG111S0058 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 10 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Ave | NG111S0058 | C.10a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Ave | NG111S0058 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Ave | NG111S0058 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Ave | NG111S0058 | J.02 | Is the Station Manual (2024 edition) known and available to station staff? | Is the Station Manual (2024 edition) known and available to station staff? | N |  | 10 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Ave | NG111S0058 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 10 Mar 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Ave | NG111S0058 | C.09a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device at the exit of the equipment? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Ave | NG111S0058 | E.12a | If "YES", is this separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET01. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Ave | NG111S0058 | K.16 | Are the PV system and inverters correctly identified with pictograms and safety + regulatory signage dedicated to solar energy? | Plan to bring signage on the site's photovoltaic installations into compliance. | N |  | 10 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Ave | NG111S0058 | D.06b | Are the station's leak detection systems operational? | Repair any leak detectors that are out of order. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Ave | NG111S0058 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 10 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | B.16 | Does the station have a general emergency stop button ? | Install a general emergency stop button for the station. | N |  | 24 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | C.09 | Are waters from the forecourt area collected and sent to a oil separator? | Plan to install a forecourt oil separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | D.05 | Are overfill protection devices installed in each of the fuel tank compartments on the site? | Install overfill protection devices on all fuel tanks on site. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | H.07 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for oil separators. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | H.08 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 24 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | E.12 | Is the offloading area connected to an oil separator, shared with the forecourt or dedicated to the offloading? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | B.13a | Is this generator equipped with an automatic source inverter? | Provide a no-load changeover procedure for use of the station genset manual source inverter. | N |  | 24 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | C.08 | Is the forecourt equipped with gutters to collect drips and runoff water from the fuel distribution? | Plan to install gutters and collect drainages to collect water from the forecourt. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | C.10 | Is the offloading area connected to an oil separator? | Install a separator or connect the offloading area to the forecourt separator. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | H.04 | Is the lighting of washing areas sufficient and operational? | Plan to revamp the lighting in the carwash area. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | H.05 | Are the gutters for collecting carwash waters connected to an oil separator (different from the one of the forecourt / offloading but common with the one from the bay possible)? | Plan to install and connect the carwash area to a oil separator (Invariant ET02). | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | H.06 | Is the carwash separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.08 | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | Are the gutters for collecting water from the bay connected to a dedicated oil separator (different from the one for forecourt / offloading)? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 24 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.19 | Is the used oil tank equipped with a retention basin? | Are used oils stored in an above-ground tank with a retention basin? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | J.17 | Does the station have an Asbestos Report, enabling precise identification of the nature and location of asbestos-contaminated materials and products on site? | Plan for an asbestos-specific technical survey to be carried out on site by an inspection body. | N |  | 24 Aug 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Western Bye Pass Minna | NG111S0282 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | E.01 | Can the fuel truck access the offloading area in forward gear, without manoeuvring? | Can the fuel delivery truck access the offloading area in forward gear, without manoeuvring? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | G.01 | Can all the bay's equipment be shut down by a dedicated emergency stop button? | Can all the bay's equipment be shut down by an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | G.03 | Is the service bay equipped with “no smoking” signs? | Plan to install “no smoking” signs in the bay. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | H.03 | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | Are all rollovers and other mobile washing equipment correctly positioned to avoid any risk of crushing during use? (minimum 50 cm from walls) | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | G.12 | Is the bay inside lighting sufficient and operational? | Plan to revamp the bay lighting. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | H.02 | Are carwash installations equipped with an emergency stop button? | Are carwash installations equipped with an emergency stop button? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | G.18 | Are used oils stored in a double-walled tank? | Are used oils stored in a double-walled underground tank? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | G.22 | Are used batteries collected and properly treated? | Are used batteries collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | G.20 | Is used oil collected and properly treated? | Is used oil collected and properly treated? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 Sep 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | G.23 | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | Is the service bay equipped with an adequately sized safety cage for inflating all types of tire? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | G.21 | Is the bay's other waste sorted into hazardous and non-hazardous waste? | Is the bay's other waste sorted into hazardous and non-hazardous waste? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | G.24 | Are used tires collected and processed appropriately? | Are used tires collected and processed appropriately? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 19 Dec 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Wudil Road | NG111S0352 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | B.17a | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | Does the report include a resistance measurement for the station's grounding system? And is it less than 10 ohms? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | D.06 | Are all the station's fuel tanks double-walled? | Are all the station's fuel tanks double-walled? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | D.16 | Does the station have a graduated gauge ruler in good condition, allowing manual gauging to be carried out? | Provide a gauging ruler to the station. | N |  | 19 Feb 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | G.14 | Have regulatory inspections of elevators and other bay equipment been carried out within the last year? | Plan for regulatory inspections of bay equipment. | N |  | 19 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | G.09 | Is the bay separator equipped with a coalescing filter and a shut-off system with a visible and functional floatting device and at the equipment exit? | Plan to replace the existing separator with an equipment compliant with invariant ET02. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | G.10 | Is the separator maintained via a specific maintenance contract, including waste management and disposal? | Plan to set up a dedicated maintenance contract for separators. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | G.11 | Are reports of the oil separator maintenance and cleaning visits available on site? | Are reports of the oil separator maintenance and cleaning visits available on site? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | G.13 | Are elevators and other mobile equipment in the bay positioned correctly to avoid any risk of crushing during handling (80cm) ? | Move mobile equipment to avoid the risk of crushing. | N |  | 19 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Bye Pass | NG111S0324 | B.17b | Have all the anomalies identified in the electrical installation inspection report been corrected? | Carry out the removal of anomalies present in the electrical installation inspection report. | N |  | 19 May 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | B.05 | Do the station's electrical installations display an 'ELECTRICAL DANGER' pictogram? | Install “ELECTRICAL DANGER” pictograms on electrical installations | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | B.10 | Are there any visible temporary electrical installations (exposed and cut wires, extension cords, dominoes, transformers on the ground, etc.)? | Plan work to bring electrical installations up to standard in order to remove temporary electrical installations from the site. | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | B.02 | Is there an updated plan of the station's electrical installations available on site near the electric board? | Provide an up-to-date diagram of the electrical installations on the station. | N |  | 19 Jun 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | C.07 | Is the feet of dispensing equipment oil-tight: lean concrete or tight sumps to prevent drips from leaking into the ground? | Provide for tightness under dispensers in accordance with invariant EP08. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | D.03 | Is the station equipped with an Automatic Gauging System (ATG)? | Plan to install an Automatic Gauging System on site. | N |  | 01 Jan 2027
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | D.14 | Are the chimneys/sumps equipped with fuel detection sensors ? | Install fuel detection sensors in chimneys above tanks. | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | D.25 | Are there any other types of check valves valves on the suction pipes or at the manhole plate? | Remove other valves to prevent product retention in pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | D.21 | Are all the station's fuel piping installations made of HDPE (High Density PolyEthylene): NUPI, KPS or UPP brands only? | Non-HDPE piping must be replaced to comply with invariant EP05. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | D.22 | Are the station's offloading pipes made of HDPE and double-walled? | Plan to replace offloading pipes with double-walled pipes. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | D.23 | Is there a compliant pipe integrity test report available for this station? | Is an integrity test less than 10 years old available for fuel pipings? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | J.04 | If the station has a shop, is it equipped with showers and changing rooms for staff? | If the station has a shop, is it equipped with showers and changing rooms for staff? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | D.24 | Are RISBRIDGER check valves present on all pipes at the feet of all dispensers? | Install or replace existing check valves with RISBRIDGER valves. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | J.05 | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | Does the station have a booklet of Daily Prevention Plans for work carried out by outside contractors? | N |  | 31 Dec 2026
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | D.20b | Have these single-walled tanks been coated/stratified? | Have these single-walled tanks been coated/stratified? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | D.20c | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | Does the concrete pit have a monitoring well to check the condition of the inside of the pit? | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | D.20d | Is an integrity test less than 5 years old available for each single-walled tank? | Plan an new integrity test for the station's single-walled tanks. | N |  | 31 Dec 2030
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | K.18 | Is a layout of the site's electrical installations, including the PV installations implementation, available on site, near the PV inverters? | Update the site's electrical layouts to include PV installations. | N |  | 19 Dec 2025
AFR | NIGERIA | TotalEnergies Marketing Nigeria PLC | Zaria Road | NG111S0364 | D.34 | Is the pre-equipment (or equipment) for Vapour Recovery Stage 1 done on site? | Plan the station vapor recovery pre-equipment to comply with EP03. | N |  | 31 Dec 2030

## Questions
Zone | Sub-Zone | Affiliate | Station Name | Station Code | Inspector | A.00 | A.01 | A.02 | A.03 | A.04 | A.05 | A.06 | A.07 | A.07a | A.07b | A.08 | A.09 | A.10 | A.10a | A.11 | A.11a | A.11b | B.01 | B.02 | B.03 | B.04 | B.05 | B.06 | B.07 | B.07a | B.08 | B.09 | B.09a | B.09b | B.10 | B.11 | B.12 | B.13 | B.13a | B.13b | B.13c | B.14 | B.15 | B.16 | B.16a | B.16b | B.17 | B.17a | B.17b | C.01 | C.02 | C.03 | C.04 | C.05 | C.06 | C.07 | C.08 | C.08a | C.08b | C.08c | C.09 | C.09a | C.09b | C.09c | C.10 | C.10a | C.10b | C.10c | C.11 | C.11a | C.11b | C.11c | C.12 | C.12a | C.12b | C.13 | C.14 | C.15 | C.15a | C.16 | D.01 | D.02 | D.02a | D.02b | D.02c | D.02d | D.02e | D.02f | D.02g | D.02h | D.02i | D.02j | D.02k | D.02l | D.02m | D.02n | D.02o | D.02p | D.02q | D.02r | D.03 | D.04 | D.04a | D.04b | D.04c | D.05 | D.05a | D.06 | D.06a | D.06b | D.07 | D.08 | D.09 | D.10 | D.11 | D.12 | D.13 | D.14 | D.15 | D.16 | D.17 | D.18 | D.19 | D.20 | D.20a | D.20b | D.20c | D.20d | D.21 | D.22 | D.23 | D.24 | D.25 | D.26 | D.27 | D.28 | D.29 | D.30 | D.31 | D.32 | D.33 | D.34 | D.35 | D.36 | D.37 | E.01 | E.02 | E.03 | E.04 | E.05 | E.06 | E.07 | E.08 | E.09 | E.10 | E.11 | E.11a | E.12 | E.12a | E.12b | E.12c | EP01 | EP02 | EP03 | EP04 | EP05 | EP06 | EP07 | EP08 | EP09 | EP10 | EP11 | ES01 | ES02 | ES03 | ES04 | ES05 | ES06 | ES07 | ES08 | ES08.a | ES09 | ES09.a | ET01 | ET02 | ET02.a | ET03 | ET04 | ET05 | F.01 | F.01a | F.01b | F.01c | F.01d | F.01e | F.01f | F.01g | F.01h | F.01i | F.01j | F.01k | F.01l | F.02 | F.02a | F.02b | F.02c | F.02d | F.02e | F.02f | F.02g | F.02h | G.00 | G.01 | G.02 | G.03 | G.04 | G.05 | G.06 | G.07 | G.08 | G.09 | G.10 | G.11 | G.12 | G.13 | G.14 | G.15 | G.16 | G.17 | G.18 | G.19 | G.20 | G.21 | G.22 | G.23 | G.24 | H.00 | H.01 | H.02 | H.03 | H.04 | H.05 | H.06 | H.07 | H.08 | Info.00 | Info.01 | Info.02 | Info.03 | Info.04 | Info.05 | Info.06 | Info.07 | Info.07a | Info.07b | Info.08 | Info.09 | Info.10 | Info.10a | Info.11 | Info.11a | Info.11b | J.01 | J.02 | J.03 | J.04 | J.05 | J.06 | J.07 | J.07a | J.08 | J.09 | J.10 | J.11 | J.11a | J.11b | J.11c | J.12 | J.12a | J.13 | J.13a | J.13b | J.13c | J.14 | J.15a | J.15b | J.16a | J.17 | J.18 | J.18a | J.19 | J.19a | J.20 | J.20a | J.20b | J.20c | J.24 | J.25 | J.26 | J.27 | K.00 | K.01 | K.02 | K.03 | K.04 | K.05 | K.06 | K.07 | K.08 | K.09 | K.10 | K.11 | K.12 | K.13 | K.14 | K.15 | K.16 | K.17 | K.18 | K.19 | K.20 | K.21 | K.22 | K.23 | L.00 | L.01 | L.02 | L.03 | L.04 | L.05 | L.06 | L.07 | L.08 | L.09 | L.10 | L.11 | L.12 | QAS24.EP01 | QAS24.EP02 | QAS24.EP04 | QAS24.EP05 | QAS24.EP06 | QAS24.EP07 | QAS24.EP08 | QAS24.EP09 | QAS24.EP10 | QAS24.EP11 | QAS24.ES01 | QAS24.ES02 | QAS24.ES03 | QAS24.ES05 | QAS24.ES06 | QAS24.ES07 | QAS24.ES08 | QAS24.ES09 | QAS24.ET01 | QAS24.ET04 | QAS24.ET05
AFR | ACE | TotalEnergies Marketing Kenya PLC | Abc | KE111S0107 | NA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ahero | KE111S0001 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Airport View | KE111S0047 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Amukeni | KE111S0048 | NA | Yes | No | No | No | No | No | No | Yes | No | No | No |  | No |  | No |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Annex | KE111S0318 | NA | [156 empty] | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Arcade | KE111S0049 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Athi River | KE111S0249 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bach Bomet | KE111S0343 | NA | Yes | No | No | Yes | No | No | No | No |  |  | No | No | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | No | No | No | No | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bahati | KE111S0051 | NA | Yes | No | No | No | No | Yes | No | No |  |  | Yes |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bamburi | KE411S0008 | NA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [21 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Barnabas | KE111S0293 | NA | [156 empty] | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bazaar | KE111S0002 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bombolulu | KE111S0052 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bondeni | KE111S0143 | NA | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Bungoma | KE111S0003 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | No | No | No | No | Yes | No | No | No | Yes | No | Yes | No |  | No |  | No | Yes |  | Yes | No | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Burnt Forest | KE111S0285 | NA | No | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Busia Dalda | KE111S0233 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | Yes | No | No |  |  | No | No | Yes | No | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Busia Road | KE111S0113 | NA | [17 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | [44 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Chabera | KE111S0331 | NA | [156 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes | [56 empty] | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Changamwe | KE111S0036 | NA | Yes | No | No | No | Yes | No | No | No |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Chokaa | KE111S0294 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Church Road | KE111S0043 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Clay City | KE111S0301 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Coast | KE111S0093 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | No | [25 empty] | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Dagoretti Corner | KE111S0157 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Dandora | KE111S0054 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | No |  | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Donholm | KE111S0182 | NA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Eastern Bypass | KE111S0271 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ebp Northlands | KE111S0337 | NA | [156 empty] | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Eldoret | KE111S0005 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Elgon View | KE111S0055 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Emali | KE111S0056 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embakasi | KE111S0173 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Embu | KE111S0319 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Entreprise Road | KE111S0057 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Expressway | KE111S0316 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | Yes |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Fedha | KE111S0174 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Fourways | KE111S0290 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Free Area | KE111S0124 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | No |  | No | [7 empty] | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Front View | KE111S0058 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Furaha | KE111S0183 | NA | [240 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gachie | KE111S0321 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ganjoni | KE111S0134 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gatitu | KE111S0007 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gigiri | KE111S0273 | NA | Yes | No | No | No | No | Yes | No | Yes | No | No | No |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gilgil | KE111S0008 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Gitaru | KE111S0309 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Githunguri | KE111S0009 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | No |  |  |  | No |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Homabay | KE111S0010 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Hurligham | KE111S0050 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ilmashariani | KE111S0277 | NA | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Isinya | KE111S0221 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | No | Yes | No | Yes | Yes | No | Yes | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Jomoko | KE111S0304 | NA | [156 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | No |  | No | Yes |  | Yes | No | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Juja | KE111S0251 | NA | No | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Juja Capital | KE111S0291 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kagwe | KE111S0012 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kakamega | KE111S0118 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | No | No | No | Yes | No |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kamakis | KE111S0312 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kamasi | KE111S0102 | NA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kamulu | KE111S0235 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kamwangi | KE111S0060 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kanduyi | KE111S0014 | NA | Yes | No | No | No | Yes | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangemi | KE111S0015 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kangundo Road | KE111S0123 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapenguria | KE111S0171 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | No | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsabet | KE111S0061 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [10 empty] | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kapsoya | KE111S0193 | NA | [156 empty] | No | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | No | Yes | Yes | Yes | No | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karambee | KE111S0062 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | No |  | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karatina | KE111S0163 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karen | KE111S0063 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Karen Kerarapon | KE111S0314 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kariokor | KE111S0119 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kasarani | KE411S0009 | NA | [156 empty] | No | No | No | Yes | Yes | No | Yes | No | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | No | No | [56 empty] | No | No | No | No | No | No | Yes | No |  |  | No | No | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kathwana | KE111S0242 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kenyatta | KE111S0064 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kericho Star | KE111S0120 | NA | No | No | No | No | Yes | No | No | No |  |  | No | No | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kerugoya | KE111S0065 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kiambu | KE111S0121 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibuye | KE111S0092 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kibwezi | KE111S0324 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kijauri | KE111S0332 | NA | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kilgoris | KE111S0168 | NA | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kilifi | KE111S0340 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kimathi Street | KE111S0153 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kimende | KE111S0240 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kiminini | KE111S0184 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kipsigis | KE111S0016 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kiserian | KE111S0066 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kisii | KE111S0067 | NA | Yes | No | No | No | No | Yes | No | Yes | No | No | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kisii Mashauri | KE111S0195 | NA | Yes | No | No | No | Yes | No | No | Yes | No | No | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | No | Yes | No | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale | KE111S0111 | NA | No | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | No | No | No | Yes | Yes | Yes | No | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | No |  | Yes | No | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Laini Moja | KE111S0068 | NA | No | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | Yes | No | Yes | No | No | No | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | No | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitale Milimani | KE111S0329 | NA | [156 empty] | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitengela | KE111S0225 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitisuru | KE111S0217 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kitui | KE111S0069 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kizingo | KE411S0002 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | [17 empty] | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Kokotoni | KE411S0006 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | No | No | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Komarock | KE111S0259 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes |  | Yes | No |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Laikipia Road | KE111S0071 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lake Naivasha | KE111S0341 | NA | [156 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Likoni Elf | KE111S0017 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Likoni Ferry | KE111S0125 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Likoni Road | KE111S0126 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Limuru Road | KE111S0154 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lokichoggio | KE111S0019 | NA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | No |  | Yes | No | Yes | No | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Luanda | KE111S0323 | NA | [156 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lumumba Avenue | KE111S0145 | NA | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [17 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Lusaka Road | KE111S0112 | NA | Yes | No | No | No | Yes | No | No | Yes | No | No | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Machakos | KE111S0020 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [21 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Madaraka | KE111S0127 | NA | [156 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | Yes | No | No |  |  | No | No | No | No | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Magadi Road | KE111S0172 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mai Mahiu | KE111S0272 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Makindu | KE111S0338 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No |  | No |  | Yes | Yes |  | Yes | No | Yes | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | No | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Makutano | KE111S0224 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Makuyu | KE111S0238 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  | No | Yes |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Malindi Arcade | KE111S0129 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Maseno | KE111S0075 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | No | No | No | Yes | Yes | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | No | No | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Matasia | KE111S0281 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Maua | KE111S0308 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mbagathi Road | KE111S0117 | NA | No | No | No | No | No | No | No | No |  |  | Yes |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Membley | KE111S0254 | NA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Meru Stage | KE111S0180 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | No |  | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Meru Town | KE111S0133 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Migori | KE111S0295 | NA | [156 empty] | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mihango | KE111S0311 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Milimani | KE111S0024 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | No |  | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mkomani | KE111S0076 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | [17 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Moi Avenue | KE411S0001 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Moi Road | KE111S0135 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Molo | KE111S0142 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mombasa Road | KE111S0100 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | [26 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mountain View | KE111S0077 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mowlem | KE111S0339 | NA | [156 empty] | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mtito Andei | KE111S0078 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mtwapa | KE111S0186 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | No | No | [56 empty] | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mua View | KE111S0317 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No |  | No |  | Yes | Yes |  | Yes | No | Yes | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | No | No | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Muhoya | KE111S0138 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mumias | KE111S0027 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | No | No | No | No | No | No | No | Yes | No | No | No |  | No |  | No | No |  | Yes | Yes | Yes | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | Yes | No | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Muranga | KE111S0166 | NA | Yes | No | No | No | No | No | No | No |  |  | Yes |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Muthaiga | KE111S0079 | NA | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | No | No | Yes | No | No |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mutituni | KE111S0275 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | No | No |  | No |  | Yes | Yes |  | Yes | No | Yes | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | No | No | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwea | KE111S0347 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwembe Tayari | KE111S0156 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | No | [25 empty] | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mwihoti | KE111S0080 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | No |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [10 empty] | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Mytown Karen | KE111S0330 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nairobi Road | KE111S0258 | NA | [156 empty] | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | No | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha | KE111S0028 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naivasha H/Way | KE111S0150 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nakuru | KE111S0306 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nakuru Highway | KE111S0185 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nakuru Town | KE111S0114 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Namanga | KE111S0227 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | No | No | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nandi Hills | KE111S0141 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | No |  | Yes | No | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nanyuki | KE111S0137 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Narok | KE111S0029 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Naromoru | KE111S0030 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Bungoma | KE111S0104 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | No | Yes | No | No | No |  | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Emali | KE111S0205 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No |  | No |  | Yes | Yes |  | No | No | No | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | No | Yes | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Gilgil | KE111S0128 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Isiolo | KE111S0160 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Jomvu | KE111S0122 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [21 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | [17 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Karibuni | KE111S0081 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Kisii | KE111S0144 | NA | Yes | No | No | No | No | No | No | Yes | Yes | No | No |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Kitui | KE111S0099 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Mumias | KE111S0139 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | No | No | No | No | Yes | No |  | No | No |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Sila | KE111S0082 | NA | Yes | No | No | No | No | No | No | Yes | No | No | No |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | New Sotik | KE111S0165 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ngara | KE111S0031 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ng'Arua | KE111S0032 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | No | No | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ngenia | KE111S0033 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ngong Road | KE111S0083 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Njabini | KE111S0151 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | No |  | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nkubu | KE111S0034 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [33 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nyahururu | KE111S0131 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Nyali Links | KE111S0289 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | No | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ol Kalou | KE111S0035 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Oljabet | KE111S0342 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Olooltepes | KE111S0236 | NA | [156 empty] | No | No | No | No | No | No | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | Yes |  | Yes | No |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ongata Rongai | KE111S0190 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Outering | KE111S0084 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | No | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rabai Road | KE111S0155 | NA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rhino | KE111S0085 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ridgeways | KE111S0220 | NA | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | No | Yes | Yes | No |  |  |  | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rongai | KE111S0086 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Rosslyn | KE111S0274 | NA | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | No |  | Yes | Yes |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ruaraka | KE111S0310 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes | [56 empty] | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ruiru Imani | KE111S0327 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ruiru Junction | KE111S0320 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ruiru Kimbo | KE111S0315 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sagana Bridge | KE111S0326 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sagana River | KE111S0344 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Shariani | KE411S0111 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | No |  | No | [7 empty] | No | [18 empty] | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sigona | KE111S0299 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sosiani River | KE111S0132 | NA | No | No | No | No | No | No | No | No |  |  | Yes | No | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | Yes | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Sotik | KE111S0037 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | South B | KE111S0136 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | South C | KE111S0038 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Spaki | KE111S0146 | NA | Yes | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Spring Valley | KE111S0116 | NA | Yes | No | No | Yes | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No |  |  |  | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Starehe | KE111S0088 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | State House Road | KE111S0115 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Supastop Sultan | KE111S0346 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Survey | KE111S0140 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Syokimau | KE111S0300 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Tala | KE111S0147 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | No | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | No | No | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Temple Road | KE111S0089 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Tezo | KE111S0335 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thika | KE111S0091 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thika Highway | KE111S0167 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thika Road | KE111S0090 | NA | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thindigua | KE111S0307 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Thome | KE111S0298 | NA | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Total Ngong | KE111S0280 | NA | [156 empty] | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Tsavo Park | KE111S0095 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Two Rivers | KE111S0325 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uganda Road | KE111S0040 | NA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Ukunda | KE111S0148 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Utalii | KE111S0096 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Utawala | KE111S0269 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru | KE111S0097 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Uthiru 87 | KE111S0212 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Voi | KE111S0169 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Waiyaki Way | KE111S0103 | NA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Wangige | KE111S0044 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Wareng | KE111S0110 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Watamu | KE111S0213 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No |  | No |  | Yes | Yes |  | Yes | No | Yes | [56 empty] | Yes | No | No | No | No | No | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Kenya PLC | Webuye | KE111S0276 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Westend | KE111S0046 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Wote | KE111S0243 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No |  | No |  | Yes | Yes |  | Yes | No | Yes | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | No | Yes | No
AFR | ACE | TotalEnergies Marketing Kenya PLC | Zambezi | KE111S0292 | NA | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | Yes | Yes | [56 empty] | Yes | No | No | No | No | Yes | No | No |  |  | No | No | No | Yes | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Airport Junction | MW111S4051 | NA | [156 empty] | Yes | No | No | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | No | Yes | Yes
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Causeway | MW111S3019 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | No | No | No | Yes | Yes | No | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Chezi | MW111S4049 | NA | [156 empty] | No | No | No | No | No | No | Yes | No | Yes | No | No | Yes | No | No | No | Yes | No | Yes | No |  | No |  | Yes | No |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Chichiri | MW111S3001 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | No | No | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | No |  | No | [7 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Chikwawa Road | MW111S3017 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [31 empty] | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dalton | MW111S4035 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Dedza | MW111S4019 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | No | No | No |  | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | No | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | No | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Ekwandeni | MW111S4020 | NA | [156 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Golomoti | MW111S4048 | NA | [156 empty] | No | No | No | No | No | No | Yes | No | Yes | Yes | No | Yes | No | No | No | Yes | No | Yes | No |  | No |  | Yes | No |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Haile Selassie | MW111S4037 | NA | [156 empty] | No | No | No | No | No | No | Yes | No | Yes | No | Yes | Yes | No | No | No | Yes | No | Yes | No |  | No |  | Yes | No |  | No | No | Yes
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Ismail | MW111S3015 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes |  | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Kamuzu Road | MW111S4050 | NA | [156 empty] | No | No | No | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | No |  | Yes | No |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Kanjedza | MW111S3021 | NA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes |  | No | [31 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [31 empty] | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Kristwick | MW111S3067 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | [28 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | No | No | No | Yes | Yes | No | No | [17 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Limbe Churchill | MW111S3022 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | No | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes |  | Yes | No | No | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | No |  | No | [7 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Limbe Lonhro | MW111S3023 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Mchinji | MW111S3039 | NA | [156 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Mount Pleasant | MW111S3018 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | No |  |  | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [8 empty] | No | [24 empty] | Yes | Yes | No | No | No | Yes | Yes | No | No | [17 empty] | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Mpingwe | MW111S3014 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Muloza | MW111S4004 | NA | [156 empty] | No | No | No | No | No | No | Yes | No | Yes | No | No | Yes | No | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Nchalo | MW111S3016 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | No | Yes | No |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Ndirande | MW111S3012 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | No | No | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | No | No | No | Yes | No | Yes | No | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | No |  | No | [7 empty] | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Polytechnic | MW111S3045 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | No | No | No | No | Yes | No | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [31 empty] | No
AFR | ACE | TotalEnergies Marketing Malawi Ltd | Thyolo | MW111S3062 | NA | [156 empty] | No | No | No | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | Yes | No | Yes | No |  | No |  | Yes | No |  | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing RDC S.A. | 14e Rue | CD111S0066 | Diana KALAMBAY | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Aero | CD111S0035 | Vavi NZEZA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Badiadingi | CD111S0049 | Aimé MATONDO | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Bakayau | CD111S0043 | Diana KALAMBAY | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Benseke | CD111S0007 | Aimé MATONDO | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Bibwa | CD111S0063 | Vavi NZEZA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Cadeco | CD111S0079 | Aimé MATONDO | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Delvaux | CD111S0020 | Christelle MABIALA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Du Peuple | CD111S0028 | Roland BAKATUIPATA | Yes | No | No | No | No | No | No | No |  |  | Yes |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Echangeur | CD111S0005 | Aimé MATONDO | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Ecole | CD111S0026 | Christelle MABIALA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Eucalyptus | CD111S0034 | Vavi NZEZA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Fikin | CD111S0039 | Diana KALAMBAY | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Force | CD111S0025 | Roland BAKATUIPATA | Yes | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Gare | CD111S0010 | Dany KANKU | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Gdl | CD111S0072 | Vavi NZEZA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing RDC S.A. | Jenny II | CD111S0060 | Dany KANKU | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No |  | Yes |  | Yes | No |  | No | Yes | Yes
AFR | ACE | TotalEnergies Marketing RDC S.A. | Joli Parc | CD111S0021 | Diana KALAMBAY | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Kenge | CD111S0044 | Roland BAKATUIPATA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | Yes |  | No | Yes | No | Yes | No | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Kimpese | CD111S0019 | Roland BAKATUIPATA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Kin II | CD111S0022 | Christelle MABIALA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  |  |  | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Kingabwa | CD111S0032 | Roland BAKATUIPATA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Lemba | CD111S0031 | Vavi NZEZA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes |  | Yes | No | No | No | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Marché | CD111S0033 | Aimé MATONDO | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Mariapolis | CD111S0050 | Dany KANKU | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Mayo | CD111S0071 | Aimé MATONDO | No | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Mimosas | CD111S0057 | Christelle MABIALA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Moulaert | CD111S0023 | Vavi NZEZA | No | No | No | No | No | No | No | No |  |  | Yes |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Mpozo | CD111S0046 | Roland BAKATUIPATA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Musompo | CD111S0069 | Dany KANKU | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Ngongo Lutete | CD111S0027 | Diana KALAMBAY | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Non Stop | CD111S0037 | Dany KANKU | No | No | No | Yes | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Oua | CD111S0059 | Diana KALAMBAY | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Ozone | CD111S0064 | Christelle MABIALA | No | No | No | No | No | No | No | Yes | No | No | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Poids Lourds | CD111S0070 | Roland BAKATUIPATA | Yes | No | No | No | No | No | No | Yes | No | No | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Pont Matadi | CD111S0001 | Roland BAKATUIPATA | Yes | No | No | No | No | Yes | No | No |  |  | Yes |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Selembao | CD111S0040 | Aimé MATONDO | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Shaba | CD111S0056 | Roland BAKATUIPATA | Yes | Yes | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Stade | CD111S0058 | Vavi NZEZA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Triangle | CD111S0065 | Vavi NZEZA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing RDC S.A. | Ucc | CD111S0061 | Aimé MATONDO | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing RDC S.A. | Vangu | CD111S0011 | Dany KANKU | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Africana | TZ111S0030 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Banana Gapco | TZ211S0012 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Bonyokwa | TZ111S0165 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Clock Tower Gapco | TZ211S0015 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | East Oysterbay Gapco | TZ211S0003 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Five Star Gapco | TZ211S0025 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | No |  | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Kariakoo Gapco Star | TZ211S0018 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Makanya | TZ111S0191 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Mikumi Gapco | TZ211S0064 | NA | No | No | No | No | No | No | No | Yes | Yes | Yes | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Morogoro Gapco Star | TZ211S0063 | NA | No | No | No | No | No | No | No | Yes | Yes | Yes | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msamvu | TZ111S0032 | NA | No | No | No | No | No | No | No | Yes | Yes | Yes | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | [17 empty] | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msigani | TZ111S0145 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Msimbazi | TZ211S0021 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyanza | TZ111S0015 | NA | No | No | No | No | No | Yes | No | No |  |  | Yes |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No |  |  | Yes | Yes | Yes |  | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | No | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No | No | Yes | No | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Nyerere Rd. Gapco | TZ211S0055 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Samora Gapco Star | TZ211S0009 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Shinyanga | TZ111S0017 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | [25 empty] | Yes | No | Yes | No | No | Yes | Yes |  | No | Yes | Yes | No |  |  |  | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Singada Gapco Star | TZ211S0066 | NA | No | No | No | No | No | No | No | Yes | Yes | Yes | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Sokoine Gapco | TZ211S0067 | NA | No | No | No | No | No | No | No | Yes | Yes | Yes | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Station Rd. Gapco Star | TZ211S0056 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No | No | Yes | No | No | No | No | Yes | Yes | Yes | No | Yes | No | No | No | No | [17 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Ubungo | TZ111S0005 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru | TZ111S0006 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Uhuru Rd. Gapco | TZ211S0010 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | No | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | University | TZ111S0004 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | Usagara Gapco | TZ211S0058 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No |  |  | Yes | Yes | Yes |  | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | No | No | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Tanzania Ltd | West Oysterbay Gapco | TZ211S0011 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Acacia | UG111S2374 | NA | [332 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Acholi Road Gulu | UG111S2278 | NA | [332 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Arua | UG111S2200 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Arua-Nile | UG111S2363 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | No |  | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bahai | UG111S2459 | NA | [332 empty] | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Bakuli | UG111S2236 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Ben Kiwanuka | UG111S2201 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | No | [31 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | No |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bombo | UG111S2269 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bugabula | UG111S2380 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | No |  | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bugembe | UG111S2237 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bugiri | UG111S2268 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bugisu | UG111S2238 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bukedea | UG111S2393 | NA | [156 empty] | No | No | Yes | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | No | No | No
AFR | ACE | TotalEnergies Marketing Uganda | Bukoto | UG111S2239 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bulamu | UG111S2410 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bulenga | UG111S2461 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | Yes | No | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Buliisa | UG111S2399 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bulindo | UG111S2362 | NA | No | No | No | No | No | No | No | No |  |  | No | No | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [10 empty] | No
AFR | ACE | TotalEnergies Marketing Uganda | Buloba | UG111S2395 | NA | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No |  |  | No | No | No | Yes | No | No | Yes |  | Yes | Yes |  |  | Yes | No | [13 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  |  |  | No | [19 empty] | Yes | No | [18 empty] | Yes | Yes |  |  |  | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Buloba Center | UG111S2417 | NA | [156 empty] | No | No | No | No | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | No | No | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Bunga | UG111S2452 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bunyonyi | UG111S2272 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Busia | UG111S2420 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Busunju | UG111S2435 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Buwate | UG111S2412 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Buwate 2 | UG111S2463 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise | UG111S2260 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bwaise - Kikoni | UG111S2274 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Bweyale | UG111S2442 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Bweyogerere | UG111S2275 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | City centre | UG111S2276 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Clock Tower | UG111S2373 | NA | No | No | No | No | No | No | Yes | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Gayaza Rd | UG111S2242 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Ggaba Road | UG111S2277 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Gokhale Rd | UG111S2368 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Gulu | UG111S2203 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | No |  | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Hima | UG111S2422 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Hoima | UG111S2204 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | No | Yes | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes |  | No | [31 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Hoima - Main street | UG111S2279 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Iganga | UG111S2243 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Igara | UG111S2205 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Highway | UG111S2370 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Lake View | UG111S2220 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main | UG111S2282 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Main Street | UG111S2222 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Jinja Road | UG111S2207 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kabale | UG111S2208 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kakiri | UG111S2464 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Kalerwe | UG111S2286 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kamuli | UG111S2288 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | No |  | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kanungu | UG111S2397 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Kasese | UG111S2245 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No |  | No |  | No | Yes | No | Yes | No | No
AFR | ACE | TotalEnergies Marketing Uganda | Katakwi | UG111S2292 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Katwe | UG111S2293 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | No |  |  |  | No |  |  |  | No | No |  | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Katwe-usafi | UG111S2372 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | No |  | No |  | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kavule | UG111S2212 | NA | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kawempe | UG111S2294 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kayunga | UG111S2382 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | No |  | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kiboga | UG111S2391 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kibuli | UG111S2248 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kibuye | UG111S2296 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kihihi Site | UG111S2414 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Kijunjubwa | UG111S2385 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kimombasa | UG111S2376 | NA | No | No | No | No | No | No | Yes | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kireka | UG111S2215 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kisaasi | UG111S2462 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kisoro | UG111S2344 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | No |  | Yes | Yes | Yes | No | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kitagobwa | UG111S2428 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | Yes | No
AFR | ACE | TotalEnergies Marketing Uganda | Kitende | UG111S2436 | NA | [156 empty] | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Kitetika | UG111S2458 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kitgum | UG111S2264 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | No |  | Yes | Yes | Yes | Yes | No | No |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kitintale | UG111S2298 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kiwatule Rd | UG111S2229 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Koboko | UG111S2429 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Komaboga | UG111S2453 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kyanja | UG111S2411 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kyazanga | UG111S2217 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kyebando | UG111S2443 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera | UG111S2218 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | No |  | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera Highway | UG111S2392 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Kyengera ward | UG111S2375 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Kyenjojo | UG111S2396 | NA | [156 empty] | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Kyesiga | UG111S2467 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Lira | UG111S2249 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Lira II | UG111S2299 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Lugazi | UG111S2301 | NA | No | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | No |  | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [10 empty] | No
AFR | ACE | TotalEnergies Marketing Uganda | Luweero | UG111S2437 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Mailo Mbiri | UG111S2367 | NA | No | No | No | No | No | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | No |  | No |  | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Masaba | UG111S2304 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Masindi Center | UG111S2306 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mayuge | UG111S2355 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mbale republic | UG111S2336 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | No | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | No |  | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Sanyu | UG111S2252 | NA | No | No | No | No | Yes | No | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mbale Taxi Park | UG111S2425 | NA | No | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Lake View | UG111S2309 | NA | No | No | No | No | No | No | No | No |  |  | Yes |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mbarara Rwebikona | UG111S2253 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | [27 empty] | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [67 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mengo star | UG111S2310 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | No |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mityana | UG111S2224 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mityana Highway | UG111S2311 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mpigi | UG111S2431 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Mponwde Rd | UG111S2381 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Muhanga | UG111S2394 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Mukono | UG111S2226 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mukono -Highway | UG111S2312 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Mukono Kawuga | UG111S2295 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Munyonyo | UG111S2438 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Nabuyonga | UG111S2386 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Nabweru | UG111S2356 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Nagalama | UG111S2313 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | No |  | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Nagongera | UG111S2389 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Najjanankumbi | UG111S2314 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | No |  | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Najjera | UG111S2345 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Najjera 2 | UG111S2456 | NA | No | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [10 empty] | No
AFR | ACE | TotalEnergies Marketing Uganda | Nakasongola | UG111S2333 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | No |  | No |  | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Nakavule | UG111S2366 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Nakawa | UG111S2254 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Nalufenya Rd | UG111S2357 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Naluvule | UG111S2400 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Namasuba 1 | UG111S2255 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Namasuba II | UG111S2228 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Nangabo | UG111S2441 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | Yes | No
AFR | ACE | TotalEnergies Marketing Uganda | Nansana | UG111S2256 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  |  |  | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Nateete | UG111S2257 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Ndeeba Mbaawo | UG111S2450 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Nsambya | UG111S2258 | NA | No | Yes | Yes | Yes | Yes | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Ntungamo | UG111S2262 | NA | No | No | No | No | No | No | No | No |  |  | Yes |  | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo | UG111S2230 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Nyendo broad way | UG111S2323 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Old portbell rd | UG111S2247 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Pakwach | UG111S2338 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | No |  | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Pallisa | UG111S2388 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | No |  | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Rock View Tororo | UG111S2202 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Rubirizi | UG111S2440 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Rugombe | UG111S2231 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | No |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Ruti | UG111S2354 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Rwizi | UG111S2387 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Seeta 2 | UG111S2233 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Seeta Highway | UG111S2209 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Seguku | UG111S2351 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | No | Yes | Yes
AFR | ACE | TotalEnergies Marketing Uganda | Sironko | UG111S2340 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | No | No | No | No | No |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | No | No | No |  | No | Yes | Yes | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Soroti | UG111S2234 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Soroti star | UG111S2331 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Station Road | UG111S2235 | NA | No | Yes | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Tororo | UG111S2328 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Wakaliga | UG111S2267 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Uganda | Wampewo | UG111S2329 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Avondale | ZM111S2284 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chilenje | ZM111S2217 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chingola A | ZM111S2203 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Chipata | ZM111S4201 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Mkushi | ZM111S4204 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Zambia Ltd | Mufuchani | ZM111S2291 | NA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Zimbabwe | 12th Avenue | ZW111S0006 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | 13th Avenue | ZW111S0004 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | 4th Avenue | ZW111S0011 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Airport Road | ZW111S0054 | NA | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No |  | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Amc Kariba | ZW111S0065 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Ascot | ZW111S0001 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Automotive Precision Engineering | ZW111S0118 | NA | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | No | Yes | Yes | No | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avondale | ZW111S0030 | NA | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Avonlea | ZW111S0066 | NA | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Belgravia | ZW111S0173 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Zimbabwe | Belmont | ZW111S0010 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Budiriro | ZW111S0061 | NA | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chinhoyi Street | ZW111S0043 | NA | Yes | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chipinge Motor Spares | ZW111S0149 | NA | Yes | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chirundu | ZW111S0084 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Chisipite | ZW111S0048 | NA | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Coropark | ZW111S0068 | NA | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Dombotombo | ZW111S0049 | NA | Yes | No | No | No | Yes | No | No | Yes | Yes | No | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Emerald Hill | ZW111S0042 | NA | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Entumbane | ZW111S0012 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Fife Street | ZW111S0013 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Fort Street | ZW111S0007 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Glen View | ZW111S0051 | NA | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | No | No | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Hillcrest | ZW111S0014 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Karoi | ZW111S0085 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kensington | ZW111S0035 | NA | Yes | No | No | No | No | No | No | Yes | Yes | No | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Kwame Nkurumah | ZW111S0059 | NA | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Macheke | ZW111S0172 | NA | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marlborough | ZW111S0081 | NA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | No | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Marondera | ZW111S0057 | NA | Yes | No | No | No | Yes | No | No | Yes | No | No | No |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No |  | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Mazowe | ZW111S0053 | NA | No | No | No | No | No | No | No | Yes | Yes | Yes | No | Yes | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Motor City | ZW111S0026 | NA | Yes | No | No | No | Yes | No | No | Yes | No | No | No |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Msasa | ZW111S0082 | NA | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Nelson Mandela | ZW111S0032 | NA | Yes | No | No | No | Yes | Yes | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Parkade | ZW111S0083 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Plumtree | ZW111S0015 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | R G Mugabe 2 | ZW111S0005 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Ridgeway | ZW111S0190 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape | ZW111S0019 | NA | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Rusape 2 | ZW111S0024 | NA | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Budiriro | ZW111S0179 | NA | Yes | No | No | No | No | Yes | No | Yes | Yes | Yes | No |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | No | No |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Macheke | ZW111S0176 | NA | Yes | No | No | No | Yes | Yes | No | Yes | No | No | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | No | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Msasa | ZW111S0183 | NA | Yes | No | No | No | Yes | No | No | No |  |  | Yes |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | RVC Nyazura | ZW111S0177 | NA | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Sakubva | ZW111S0023 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora 1 | ZW111S0041 | NA | Yes | No | No | No | Yes | No | No | Yes | Yes | No | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No |  |  | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | No | Yes | No | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Samora Machel 2 | ZW111S0044 | NA | Yes | No | No | No | Yes | No | No | Yes | Yes | No | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Southworld | ZW111S0017 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Springs | ZW111S0058 | NA | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Vumba Park | ZW111S0025 | NA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No
AFR | ACE | TotalEnergies Marketing Zimbabwe | Westgate | ZW111S0155 | NA | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Croydon | SZ111S0031 | NA | [156 empty] | No | No | No | No | No | No | Yes | No | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | Yes
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Emfuleni | SZ111S0001 | NA | No | No | No | No | No | No | No | No |  |  | Yes | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | No | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ezulwini | SZ111S0024 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Gwamile | SZ111S0006 | NA | [156 empty] | No | No | No | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | Yes | No | Yes
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Hub | SZ111S0002 | NA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | No | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | No | Yes | No | Yes | Yes | No | Yes | Yes | No | No | No | No |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | No | No | Yes | No | Yes | Yes | No | No | Yes | Yes | No | No | No | No | Yes | No | No | No | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | No | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Lomahasha | SZ111S0013 | NA | [156 empty] | No | No | No | No | No | No | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ludzeludze | SZ111S0029 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | Yes | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mafutheni | SZ111S0019 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mdwali | SZ111S0005 | NA | No | No | No | No | No | No | No | No |  |  | No | No | Yes | No | No |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | No | No | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | No | No | Yes | No | No | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | No | No | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Moneni | SZ111S0007 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | No |  |  |  | No |  |  |  | Yes | No | Yes | Yes | No |  |  | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | Yes | No | Yes | No | No | No | No | Yes | Yes | No | No | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | No | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | No | Yes |  | Yes | No | No | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Mpaka | SZ111S0018 | NA | [156 empty] | No | No | No | No | No | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | No | Yes | No |  | No |  | Yes | No |  | No | No | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | New Macondza | SZ111S0011 | NA | [156 empty] | No | No | No | No | No | No | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngonini | SZ111S0020 | NA | [156 empty] | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Ngwane Park | SZ111S0023 | NA | No | No | No | No | No | No | Yes | No |  |  | No | No | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | No | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Plaza | SZ111S0003 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No | No | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | No | Yes | Yes | No | No | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Robs Garage Bottom | SZ111S0017 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | No | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Robs Garage Top | SZ111S0016 | NA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Rusi | SZ111S0021 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Sheffield | SZ111S0009 | NA | [156 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Sigodvweni | SZ111S0008 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | Yes | No | No |  |  | No | No | Yes | No | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | T Junction | SZ111S0012 | NA | [156 empty] | No | No | No | Yes | No | No | Yes | No | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | No
AFR | AFA | TotalEnergies Marketing Eswatini (PTY) Ltd | Tums | SZ111S0028 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing Namibia Pty Ltd | Divundu | NA111S0078 | NA | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | No | Yes | No |  | No |  | No | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing Namibia Pty Ltd | Sar Ombili | NA111S0097 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | 14th Avenue | ZA111S0039 | Lethabo XINZI | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [63 empty] | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | 60 On Murchinson | ZA111S0724 | Kurt GOVENDER | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Airport Industria | ZA111S0650 | Vusi MSIZA | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Ambassador Duty Free Fuel | ZA111S0532 | Khuliso NETSHIKHUDINI | [156 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | No | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Ashburton Garage | ZA111S0343 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | No | No | Yes | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | No | [56 empty] | No | No | No | No | Yes | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Atlas Road | ZA111S0713 | Mmapeu-Malucia MAKHAFOLA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Beyers Naude | ZA111S0290 | Mmapeu-Malucia MAKHAFOLA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Boiketlong | ZA111S0930 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Boschkop | ZA111S0075 | Mmapeu-Malucia MAKHAFOLA | [156 empty] | No | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Boulevard Motors | ZA111S0674 | Vusi MSIZA | [156 empty] | No | No | No | No | No | No | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | No | Yes |  | Yes | No | No | [56 empty] | Yes | No | No | No | Yes | No | No | No |  |  | No | Yes | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Brackenfell | ZA111S0192 | Vusi MSIZA | Yes | No | No | No | Yes | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Bryanston | ZA111S0462 | Mmapeu-Malucia MAKHAFOLA | Yes | No | No | No | No | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Buffelskloof | ZA111S0346 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | No | [56 empty] | No | No | No | No | Yes | No | No | No |  |  | No | No | No | Yes | No
AFR | AFA | TotalEnergies Marketing South Africa | Centurion Gate | ZA111S0142 | Khuliso NETSHIKHUDINI | [156 empty] | No | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Clayville | ZA111S0712 | Mmapeu-Malucia MAKHAFOLA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Clermont | ZA111S0697 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | No | No | Yes | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | No | No | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | Yes | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Crossmoor | ZA111S0750 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No |  | No |  | Yes | No |  | No | Yes | Yes | [56 empty] | No | No | No | No | Yes | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Dad's Pride | ZA111S0084 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | De Deur | ZA111S0959 | Lethabo XINZI | [156 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Durbanville | ZA111S0207 | Vusi MSIZA | Yes | No | No | No | Yes | Yes | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Eersterust | ZA111S0948 | Khuliso NETSHIKHUDINI | [156 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Entrance | ZA111S0434 | Khuliso NETSHIKHUDINI | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Esikhaleni | ZA111S0956 | Kurt GOVENDER | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Eversdal Motors | ZA111S0510 | Vusi MSIZA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | Yes | Yes | No | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Fairways | ZA111S0968 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Florida Lake Motors | ZA111S0033 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | Yes | No | No | Yes |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Four Way Motors | ZA111S0210 | Lethabo XINZI | [156 empty] | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Four Way Truck Stop | ZA111S0963 | Lethabo XINZI | [156 empty] | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | No | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Gamalakhe | ZA111S0363 | Kurt GOVENDER | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | No | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Gateway 1 | ZA111S0093 | Kurt GOVENDER | [156 empty] | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Glen 1 | ZA111S0025 | Thivhonali NELWAMONDO | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Glen 2 | ZA111S0006 | Thivhonali NELWAMONDO | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | No | No | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Glen Marais | ZA111S0642 | Mmapeu-Malucia MAKHAFOLA | Yes | No | No | No | No | Yes | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Glencairn | ZA111S0695 | Vusi MSIZA | Yes | No | No | No | No | No | No | Yes | No | No | Yes |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Gordon Road | ZA111S0009 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Gugulethu | ZA111S0500 | Vusi MSIZA | Yes | No | No | No | Yes | No | Yes | No |  |  | No |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | No | No |  |  | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | No |  |  |  | No |  |  | Yes | Yes | No |  |  | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | No | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | No | No | No | Yes | Yes | Yes | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Hansa Auto Services | ZA111S0065 | Khuliso NETSHIKHUDINI | Yes | No | No | No | Yes | No | Yes | No |  |  | No |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [31 empty] | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | [17 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Hartbeespoort | ZA111S0058 | Makalo KHOJANE | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Hazyview Motors | ZA111S0215 | Lebokgang MOKOENA | [156 empty] | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Helmut Motors | ZA111S0473 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | Yes | No | No | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Hluhluwe | ZA111S0218 | Kurt GOVENDER | [156 empty] | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Jabulani Garage | ZA111S0665 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | No | No | Yes | No | No | No | No | Yes | No | No | No |  | No |  | No | No |  | Yes | No | No | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Jozini | ZA111S0940 | Kurt GOVENDER | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | Yes | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | K K Motors | ZA111S0351 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | No | [56 empty] | No | No | No | No | Yes | No | No | No |  |  | No | No | Yes | Yes | Yes | Yes | No
AFR | AFA | TotalEnergies Marketing South Africa | Kampus Diensstasie | ZA111S0634 | Makalo KHOJANE | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | No |  |  |  | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Khayelitsha | ZA111S0223 | Vusi MSIZA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | No | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Kingfisher Motors | ZA111S0069 | Kurt GOVENDER | No | No | No | No | No | No | No | No |  |  | Yes |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | [17 empty] | Yes | No | Yes | No | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Kliptown | ZA111S0927 | Lethabo XINZI | [156 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Knoppieslaagte | ZA111S0941 | Khuliso NETSHIKHUDINI | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Krugersdorp | ZA111S0019 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Kuilsriver | ZA111S0226 | Vusi MSIZA | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | L D Motors | ZA111S0667 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | No | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Lakeside | ZA111S0648 | Vusi MSIZA | Yes | No | No | No | Yes | No | No | No |  |  | Yes |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Langebaan | ZA111S0227 | Vusi MSIZA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Leratong | ZA111S0066 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Madlanduma | ZA111S0233 | Kurt GOVENDER | [156 empty] | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | Yes | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Malanda | ZA111S0664 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | No | No | Yes | No | No | No | No | Yes | No | No | No |  | No |  | No | No |  | No | No | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Malanda Dlamini | ZA111S0978 | Kurt GOVENDER | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Mamelodi | ZA111S0321 | Khuliso NETSHIKHUDINI | [156 empty] | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Manjoe's | ZA111S0353 | Kurt GOVENDER | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | No | Yes | No | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Marylone | ZA111S0060 | Khuliso NETSHIKHUDINI | Yes | No | No | No | Yes | Yes | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Melkbos | ZA111S0238 | Vusi MSIZA | Yes | No | No | No | No | Yes | Yes |  |  |  | No | No | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | No | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Meredale | ZA111S0085 | Thivhonali NELWAMONDO | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Mhala Motors | ZA111S0393 | Lebokgang MOKOENA | [156 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | Yes | No | No | No | Yes | No | Yes | No |  |  | No | No | Yes | Yes | No
AFR | AFA | TotalEnergies Marketing South Africa | Midway Service Centre | ZA111S0014 | Lethabo XINZI | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Mitchell's Plein | ZA111S0240 | Vusi MSIZA | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | Yes | [56 empty] | Yes | No | No | No | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | No
AFR | AFA | TotalEnergies Marketing South Africa | Modderdam | ZA111S0241 | Vusi MSIZA | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Montague Drive Motors | ZA111S0242 | Vusi MSIZA | [156 empty] | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | Yes | [56 empty] | Yes | No | No | No | No | No | Yes | No |  |  | No | Yes | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Moot Street Motors (Pty) Ltd | ZA111S0045 | Khuliso NETSHIKHUDINI | Yes | No | No | No | Yes | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [17 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Murrayfield Motors | ZA111S0428 | Khuliso NETSHIKHUDINI | Yes | No | No | No | Yes | No | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | N1 City | ZA111S0245 | Vusi MSIZA | Yes | No | No | No | Yes | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Navy | ZA111S0921 | Kurt GOVENDER | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | Yes | No
AFR | AFA | TotalEnergies Marketing South Africa | Newtown | ZA111S0076 | Mmapeu-Malucia MAKHAFOLA | Yes | No | No | No | Yes | No | Yes | No |  |  | No |  | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Nono's | ZA111S0660 | Vusi MSIZA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | No | No | Yes | No | Yes | Yes |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | No | [7 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Norkem Park | ZA111S0533 | Mmapeu-Malucia MAKHAFOLA | Yes | No | No | No | Yes | Yes | Yes | No |  |  | Yes |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No | [24 empty] | No | [25 empty] | Yes | No | Yes | No | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Oasis | ZA111S0345 | Kurt GOVENDER | [156 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | Yes | No | No | Yes | No
AFR | AFA | TotalEnergies Marketing South Africa | Observatory | ZA111S0249 | Vusi MSIZA | Yes | No | No | No | Yes | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Ohlanga Auto City | ZA111S0358 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | No | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Orange Farm | ZA111S0072 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | No | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Orlando | ZA111S0037 | Lethabo XINZI | Yes | No | No | No | Yes | No | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | No | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Osizweni Garage | ZA111S0668 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | No | No | Yes | No | No | No | No | Yes | No | No | No |  | No |  | No | No |  | No | No | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | Yes | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Paarden Eiland | ZA111S0522 | Vusi MSIZA | Yes | No | No | No | Yes | No | No |  |  |  | Yes | Yes | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Paarl Mall | ZA111S0366 | Vusi MSIZA | Yes | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | [23 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Palm Springs | ZA111S0657 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | No | Yes | Yes | Yes | No | No | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Panorama | ZA111S0253 | Vusi MSIZA | [156 empty] | No | No | No | No | No | No | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | No | Yes |  | Yes | No | No | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | Yes | Yes | Yes | No
AFR | AFA | TotalEnergies Marketing South Africa | Parklands | ZA111S0254 | Vusi MSIZA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Pecanwood | ZA111S0036 | Makalo KHOJANE | Yes | No | No | No | Yes | No | Yes | Yes | No | No | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria North | ZA111S0070 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Petroport N14 - Lanseria South | ZA111S0071 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | No | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Petroport Panorama East | ZA111S0110 | Khuliso NETSHIKHUDINI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Petroport Panorama West | ZA111S0109 | Khuliso NETSHIKHUDINI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Petroport Piketberg | ZA111S0286 | Vusi MSIZA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Pierre Van Ryneveld | ZA111S0040 | Khuliso NETSHIKHUDINI | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Pilditch Motors | ZA111S0299 | Khuliso NETSHIKHUDINI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | No | Yes | No | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Pimville College | ZA111S0056 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | Yes | No | No | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | No | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Portlands | ZA111S0675 | Vusi MSIZA | [156 empty] | No | Yes | No | No | No | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | No | No |  | Yes | No | No | [56 empty] | Yes | No | No | No | Yes | No | Yes | No |  |  | No | Yes | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Portugal Motors | ZA111S0458 | Mmapeu-Malucia MAKHAFOLA | [156 empty] | No | No | No | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Pretoriuskop | ZA111S0800-J | Lebokgang MOKOENA | [156 empty] | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | No |  | No | No |  | Yes | No | Yes | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Quellerie Park | ZA111S0292 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | R566 Brits | ZA111S0723 | Makalo KHOJANE | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Ramsgate | ZA111S0173 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | No | No | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | Yes | Yes | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Rand | ZA111S0032 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | [17 empty] | Yes | No | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Randgate | ZA111S0259 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Rangeview | ZA111S0529 | Lethabo XINZI | Yes | No | No | No | No | No | No | No |  |  | Yes |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Renbro Service Centre | ZA111S0328 | Khuliso NETSHIKHUDINI | Yes | No | No | No | Yes | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Rhino | ZA111S0111 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Richards Drive | ZA111S0001 | Khuliso NETSHIKHUDINI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Richwood | ZA111S0261 | Vusi MSIZA | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Riverside | ZA111S0182 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Robert Broom | ZA111S0051 | Lethabo XINZI | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Robertsham | ZA111S0101 | Thivhonali NELWAMONDO | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | [17 empty] | No | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Rock Cottage | ZA111S0018 | Lethabo XINZI | Yes | No | No | No | No | Yes | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [17 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | Yes | No | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Rosslyn Petro City 1 | ZA111S0124 | Khuliso NETSHIKHUDINI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | [31 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Rosslyn Petro City 2 | ZA111S0138 | Khuliso NETSHIKHUDINI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Rosslyn Service Centre | ZA111S0030 | Khuliso NETSHIKHUDINI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Saldanha | ZA111S0649 | Vusi MSIZA | Yes | No | No | No | No | No | No | No |  |  | Yes |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Sebokeng | ZA111S0177 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | No | No | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Simonsrust | ZA111S0267 | Vusi MSIZA | [156 empty] | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes |  | Yes | Yes | No | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | Yes | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Skukuza | ZA111S0800-L | Lebokgang MOKOENA | [156 empty] | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | No | Yes | Yes | Yes | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Somerset Mall | ZA111S0268 | Vusi MSIZA | Yes | No | No | No | No | Yes | No |  |  |  | No | Yes | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | South Coast | ZA111S0119 | Kurt GOVENDER | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | No |  |  |  | No |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | No | Yes | No | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | St Helena Bay | ZA111S0524 | Vusi MSIZA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | No | No |  | Yes | No | No | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | Yes | No | Yes | Yes | No
AFR | AFA | TotalEnergies Marketing South Africa | Stikland | ZA111S0270 | Vusi MSIZA | Yes | No | No | No | Yes | No | Yes | No |  |  | No | Yes |  |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Strand | ZA111S0272 | Vusi MSIZA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Summit Road | ZA111S0714 | Khuliso NETSHIKHUDINI | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Sun Valley | ZA111S0438 | Khuliso NETSHIKHUDINI | Yes | No | No | No | No | Yes | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | No | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Sunningdale | ZA111S0955 | Vusi MSIZA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Table View | ZA111S0276 | Vusi MSIZA | Yes | No | No | No | Yes | No | No |  |  |  | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Technicon | ZA111S0421 | Khuliso NETSHIKHUDINI | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | No | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Three Way Motors | ZA111S0053 | Khuliso NETSHIKHUDINI | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Tokai | ZA111S0275 | Vusi MSIZA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [21 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Twin Cities | ZA111S0794 | Makalo KHOJANE | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFA | TotalEnergies Marketing South Africa | Umhlali | ZA111S0752 | Kurt GOVENDER | [156 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Ushaka | ZA111S0092 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | No
AFR | AFA | TotalEnergies Marketing South Africa | Viking | ZA111S0281 | Vusi MSIZA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | [17 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Volta | ZA111S0659 | Lethabo XINZI | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Waltloo | ZA111S0023 | Khuliso NETSHIKHUDINI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Weltevredenpark | ZA111S0106 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | No | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Westgate | ZA111S0731 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Wilcor Motors | ZA111S0647 | Lethabo XINZI | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | William Nicol | ZA111S0017 | Mmapeu-Malucia MAKHAFOLA | Yes | No | No | No | No | No | Yes | No |  |  | Yes |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Winchester Hills | ZA111S0003 | Thivhonali NELWAMONDO | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Wingate | ZA111S0374 | Kurt GOVENDER | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No |  | No |  | No | No |  | No | No | No | [56 empty] | No | No | No | No | No | No | No | No |  |  | No | No | No | No | Yes | Yes | No
AFR | AFA | TotalEnergies Marketing South Africa | Witpoortjie | ZA111S0486 | Lethabo XINZI | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | No | No | No | Yes | Yes | Yes | Yes | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | No | Yes | Yes | No | No | No | No | [17 empty] | No | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Wonderboom South | ZA111S0090 | Khuliso NETSHIKHUDINI | Yes | No | No | No | Yes | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Woodstock | ZA111S0287 | Vusi MSIZA | Yes | No | No | No | Yes | No | No | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFA | TotalEnergies Marketing South Africa | Zandspruit | ZA111S0288 | Mmapeu-Malucia MAKHAFOLA | [156 empty] | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | 37 Hospital Road | GH111S0001 | Doris MINTA | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | No |  | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | Yes | No | No | No | Yes | Yes | Yes | No | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aboabo | GH111S0002 | Goddard AMISSAH | Yes | No | No | No | Yes | No | Yes | Yes | No | No | No |  | Yes | No | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Abossey Okai 1 | GH111S0003 | Doris MINTA | No | No | No | No | Yes | Yes | Yes | No |  |  | No | Yes | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | No | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | No |  | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aburi | GH111S0249 | Duncan TETTEY | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Accra Newtown | GH111S0007 | Doris MINTA | No | No | No | No | Yes | Yes | Yes | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Achimota Village | GH111S0009 | Doris MINTA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | No | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adabraka | GH111S0011 | Doris MINTA | No | No | No | No | Yes | No | No | No |  |  | No | Yes | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | No |  | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Adenta Barrier | GH111S0304 | Doris MINTA | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Aflao | GH111S0013 | Duncan TETTEY | No | No | No | No | No | No | No | No |  |  | No | No | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Agormanya | GH111S0017 | Duncan TETTEY | [156 empty] | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes | [56 empty] | Yes | No | No | No | No | No | No | No |  |  | No | No | Yes | No | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ahenkofikrom | GH111S0278 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akim Oda | GH111S0020 | Duncan TETTEY | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Akpokple | GH111S0022 | Duncan TETTEY | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | No |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Amanfrom East | GH111S0026 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | No | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Amanfrom West | GH111S0306 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Amanfrom West 2 | GH111S0316 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ankwa Dobro | GH111S0043 | Duncan TETTEY | [156 empty] | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Antoa Road | GH111S0028 | Goddard AMISSAH | Yes | No | No | No | Yes | No | Yes | Yes | No | No | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | No |  | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Anyaa | GH111S0248 | Doris MINTA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | No | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apenkwa | GH111S0030 | Doris MINTA | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | No | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apowa | GH111S0236 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Apremdo | GH111S0031 | Vincent ATOMBOH | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Asabahan | GH111S0334 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Atomic Energy Road | GH111S0281 | Doris MINTA | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | No | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Baatsona | GH111S0046 | Duncan TETTEY | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bamahu | GH111S0280 | Mohammed OSUMANU | [156 empty] | No | No | No | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Barima Accra | GH111S0224 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | No | No | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai | GH111S0050 | Goddard AMISSAH | Yes | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | No |  | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | No | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bekwai Lorry Park | GH111S0051 | Goddard AMISSAH | Yes | No | No | No | Yes | Yes | Yes | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Boboobo | GH111S0290 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | No | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bole | GH111S0056 | Mohammed OSUMANU | No | No | No | No | Yes | Yes | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 2 | GH111S0057 | Mohammed OSUMANU | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | No | No | No | No | Yes | No | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga 3 | GH111S0282 | Mohammed OSUMANU | [156 empty] | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Central | GH111S0058 | Mohammed OSUMANU | No | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bolga Soe | GH111S0285 | Mohammed OSUMANU | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Bronyibima | GH111S0256 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | No | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Buipe | GH111S0286 | Mohammed OSUMANU | No | No | No | No | No | No | No | Yes | No | No | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Burma Road | GH111S0060 | Goddard AMISSAH | Yes | No | No | No | Yes | Yes | Yes | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | No |  | No | [7 empty] | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Chapel Square | GH111S0065 | Vincent ATOMBOH | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Community 1 Market | GH111S0066 | Vincent ATOMBOH | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Cooperative | GH111S0069 | Doris MINTA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Daboya Road | GH111S0070 | Mohammed OSUMANU | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Dansoman Agege | GH111S0293 | Doris MINTA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Darkuman Junction | GH111S0072 | Vincent ATOMBOH | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | No |  | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Derby Avenue | GH111S0073 | Doris MINTA | No | No | No | No | Yes | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Dunkwa 1 | GH111S0076 | Goddard AMISSAH | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Effiekuma | GH111S0276 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | No | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Farrar Avenue | GH111S0082 | Duncan TETTEY | No | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Flyover | GH111S0084 | Duncan TETTEY | Yes | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Gbawe | GH111S0307 | Doris MINTA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Gopdc Kwae | GH111S0087 | Duncan TETTEY | No | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Graphic Road | GH111S0294 | Doris MINTA | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hansen Fadama | GH111S0090 | Doris MINTA | No | No | No | No | Yes | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ho Dome | GH111S0094 | Duncan TETTEY | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Hohoe | GH111S0095 | Duncan TETTEY | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Independence Avenue | GH111S0097 | Vincent ATOMBOH | No | No | No | No | Yes | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Jirapa | GH111S0099 | Mohammed OSUMANU | [156 empty] | No | No | No | No | No | No | Yes | No | Yes | No | No | Yes | No | No | No | Yes | No | No | Yes |  | No |  | No | No |  | Yes | No | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Jisonayili | GH111S0289 | Mohammed OSUMANU | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kaiser Valley | GH111S0275 | Duncan TETTEY | Yes | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kasawurodo | GH111S0291 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kasoa Overhead | GH111S0295 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kintampo | GH111S0105 | Goddard AMISSAH | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Koforidua Mile 50 | GH111S0324 | Duncan TETTEY | [156 empty] | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Koforidua Obuoman | GH111S0233 | Duncan TETTEY | [156 empty] | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Koforidua Suhum Road | GH111S0257 | Duncan TETTEY | [156 empty] | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Korle Bu | GH111S0112 | Doris MINTA | No | No | No | No | Yes | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Kwesimintsim | GH111S0116 | Vincent ATOMBOH | Yes | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Beach | GH111S0117 | Doris MINTA | No | No | No | No | Yes | Yes | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | La Paz | GH111S0253 | Doris MINTA | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Labour | GH111S0120 | Goddard AMISSAH | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Laterbiokorshie | GH111S0123 | Doris MINTA | No | No | No | No | Yes | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | Yes | No | No |  |  |  |  | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Lawra | GH111S0124 | Vincent ATOMBOH | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | No | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | No |  | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Legon 2 | GH111S0126 | Doris MINTA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Liberia Road | GH111S0206 | Doris MINTA | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | No |  | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 1 | GH111S0133 | Vincent ATOMBOH | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mallam 2 | GH111S0134 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mamfe | GH111S0135 | Duncan TETTEY | No | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Manhyia | GH111S0140 | Goddard AMISSAH | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No | Yes |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | No | No | No | No | No | Yes | Yes | No | No | No | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | Yes | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 1 | GH111S0141 | Goddard AMISSAH | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | No | No | Yes |  |  |  |  | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Maxwell 2 | GH111S0142 | Goddard AMISSAH | Yes | No | No | No | Yes | No | Yes | Yes | No | No | Yes |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Mccarthy Hill | GH111S0264 | Vincent ATOMBOH | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Medie | GH111S0234 | Duncan TETTEY | [156 empty] | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Navrongo | GH111S0148 | Mohammed OSUMANU | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | New Tafo | GH111S0153 | Goddard AMISSAH | Yes | No | No | No | No | Yes | No | No |  |  | No | No | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nim Avenue | GH111S0154 | Mohammed OSUMANU | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Nsawam | GH111S0160 | Duncan TETTEY | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obetsebi Circle | GH111S0162 | Doris MINTA | Yes | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Antobuasi | GH111S0163 | Goddard AMISSAH | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | No | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Anyinam | GH111S0164 | Goddard AMISSAH | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [17 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Tutuka | GH111S0245 | Goddard AMISSAH | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [31 empty] | No | [12 empty] | No | [8 empty] | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | No |  | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Obuasi Wawase | GH111S0165 | Goddard AMISSAH | Yes | No | No | No | Yes | No | Yes | Yes | No | No | No | No | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | No | Yes | Yes | No | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Okwenya | GH111S0314 | Duncan TETTEY | [156 empty] | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Onyadze | GH111S0241 | Duncan TETTEY | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Oxford Street | GH111S0061 | Doris MINTA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Pig Farm Junction | GH111S0172 | Doris MINTA | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Rex | GH111S0174 | Goddard AMISSAH | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | [25 empty] | Yes | Yes | Yes | No | No | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | No |  | No | [7 empty] | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ring Road | GH111S0175 | Doris MINTA | No | No | No | Yes | Yes | Yes | Yes | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Ritz Junction | GH111S0311 | Doris MINTA | [156 empty] | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sakaman | GH111S0176 | Vincent ATOMBOH | Yes | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Salaga | GH111S0250 | Mohammed OSUMANU | [156 empty] | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sokode | GH111S0269 | Duncan TETTEY | [156 empty] | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Sowutuom | GH111S0242 | Doris MINTA | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru North | GH111S0188 | Vincent ATOMBOH | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Town | GH111S0190 | Vincent ATOMBOH | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Swedru Winneba Road | GH111S0191 | Vincent ATOMBOH | Yes | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tamale Dungu | GH111S0296 | Mohammed OSUMANU | [156 empty] | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | No | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tamale Hospital Road | GH111S0193 | Mohammed OSUMANU | No | No | No | No | Yes | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tamale South | GH111S0194 | Mohammed OSUMANU | [156 empty] | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tema Hospital Road | GH111S0238 | Duncan TETTEY | Yes | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tema Industrial Area | GH111S0267 | Duncan TETTEY | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | [19 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tema Motorway 1 | GH111S0200 | Duncan TETTEY | No | No | No | No | No | No | No | No |  |  | No | No | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tesano | GH111S0202 | Doris MINTA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie | GH111S0203 | Doris MINTA | No | No | No | No | Yes | Yes | Yes | No |  |  | No |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No | No | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Teshie Tsui Bleoo | GH111S0205 | Doris MINTA | [156 empty] | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | Yes | No | No |  | No | No |  | No | No | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tuba | GH111S0313 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | No | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Tumu | GH111S0208 | Mohammed OSUMANU | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa | GH111S0209 | Mohammed OSUMANU | No | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | Yes | No | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | Yes | No | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | No | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa 2 | GH111S0210 | Vincent ATOMBOH | [156 empty] | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | Yes |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa 3 | GH111S0302 | Mohammed OSUMANU | [156 empty] | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wa Kaleo | GH111S0243 | Mohammed OSUMANU | [156 empty] | No | No | No | No | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | No | No |  | Yes | No | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Walewale | GH111S0211 | Mohammed OSUMANU | [156 empty] | No | No | No | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wassa Agona | GH111S0319 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Wassa Simpa | GH111S0326 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | No | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | West Fijai | GH111S0274 | Vincent ATOMBOH | [156 empty] | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | No |  | Yes | Yes | No | Yes | Yes | Yes
AFR | AFO | TOTAL PETROLEUM GHANA PLC | Winkogo | GH111S0214 | Mohammed OSUMANU | [156 empty] | No | No | No | No | No | No | Yes | No | No | No | No | Yes | No | No | No | No | Yes | Yes | No |  | No |  | No | No |  | No | No | No
AFR | AFO | TOTAL PETROLEUM GHANA PLC | X'Borg | GH111S0216 | Doris MINTA | No | No | No | No | Yes | Yes | Yes | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | No | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | No | No | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Abong-mbang 2 | CM111S5204 | NA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Aeroport douala | CM111S2290 | NA | Yes | No | No | No | Yes | Yes | No | Yes | Yes | Yes | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Aeroport yaounde | CM111S2211 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Akak | CM111S5221 | NA | [156 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  | Yes | No |  | Yes | Yes | Yes
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Akonolinga | CM111S2230 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Akwa 1 &amp; 2 | CM111S2286 | NA | Yes | No | No | No | Yes | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ambam 1 | CM111S2343 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Awae | CM111S2234 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Ayos | CM111S2210 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Babadjou | CM111S2324 | NA | No | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | Yes | Yes | No | No | No |  |  | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No |  |  | Yes | Yes | Yes |  | Yes | No | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | No | No | Yes | No | Yes | No | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | No |  | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang bondja | CM111S2329 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | No | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang centre | CM111S2317 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafang chefferie | CM111S2321 | NA | No | No | No | No | No | Yes | No | Yes | Yes | No | No |  | Yes | Yes | No |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | No |  |  | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafia1 | CM111S2207 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No |  |  |  | No |  | No |  |  |  | No |  |  |  | No | No |  | Yes | No | Yes | No | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bafia2 | CM111S2216 | NA | No | No | No | No | No | No | No | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | No |  | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Baham | CM111S2316 | NA | No | No | No | No | No | Yes | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | No | No | No | No | No | No | No | No | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | [28 empty] | No | [12 empty] | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | No | [7 empty] | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 1 | CM111S2341 | NA | No | No | No | No | No | No | Yes | No |  |  | Yes |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | No | Yes | Yes | No |  |  |  | Yes | No | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | No | No | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamenda 2 | CM111S2330 | NA | No | No | No | No | No | No | Yes | No |  |  | No |  | Yes | No | No |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes | Yes | No | No | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes | No | No | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | [17 empty] | No | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bamendzi | CM111S2311 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bandjoun | CM111S2315 | NA | No | Yes | No | No | No | Yes | No | Yes | Yes | No | No |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No |  | Yes | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | No | No | No | No | No | No | No | No | No | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | No |  | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bangangte 1 | CM111S2323 | NA | No | No | No | No | No | No | No | Yes | Yes | No | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | No | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | No | No | No | No | No | No | No | Yes | Yes | Yes | No | No | No | No | No | No | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | Yes | Yes | Yes | Yes | No | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bangangte 2 | CM111S2340 | NA | No | Yes | No | No | No | Yes | No | Yes | Yes | No | No |  | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No |  | Yes | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | No | No | No | No | No | No | Yes | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | No |  | Yes | No | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bangangte feumbat | CM111S5216 | NA | [156 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | No | Yes | Yes | No | No |  | Yes | Yes | Yes | Yes | Yes | Yes
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Batouri | CM111S2246 | NA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | No | No | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | No |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bd presidentiel | CM111S2206 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Beedi | CM111S2424 | NA | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Belabo | CM111S2245 | NA | Yes | No | No | No | No | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | No |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bepanda | CM111S2254 | NA | Yes | No | No | No | Yes | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bepanda yonyong | CM111S2425 | NA | No | No | No | No | No | Yes | Yes | Yes | Yes | No | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua | CM111S2410 | NA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | No |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 1 | CM111S2249 | NA | Yes | No | No | No | No | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | No | No |  |  |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | No | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes | No | Yes | Yes | No | Yes | No | Yes | No | No | No | No | Yes | Yes | No | No | No | Yes | Yes | No | No | No | No | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | No | No | No | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | No |  | No |  |  |  | No |  |  |  | No | No |  | No |  | No | [7 empty] | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bertoua 2 | CM111S2244 | NA | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | No |  | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Besseke | CM111S2352 | NA | Yes | No | No | No | No | No | Yes | Yes | No | Yes | No | Yes | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bessengue | CM111S2350 | NA | Yes | No | No | No | No | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Biteng | CM111S2405 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [26 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Biyem assi1 | CM111S2209 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Biyem assi2 | CM111S2237 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bojongo | CM111S2259 | NA | Yes | No | No | No | No | Yes | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonaberi 1 | CM111S2282 | NA | Yes | No | No | No | Yes | Yes | Yes | No |  |  | No |  | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonaberi 2 | CM111S2283 | NA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [26 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonalembe | CM111S2276 | NA | Yes | No | No | No | Yes | Yes | Yes | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonamoudourou | CM111S2260 | NA | Yes | No | No | No | No | Yes | Yes | No |  |  | No | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonamoussadi 1 | CM111S2295 | NA | Yes | No | No | No | No | No | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonamoussadi 2 | CM111S2356 | NA | Yes | No | No | No | No | No | Yes | Yes | Yes | No | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [50 empty] | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonateki 2 | CM111S2275 | NA | Yes | No | No | No | Yes | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | No | [31 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Bonis | CM111S2417 | NA | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | No |  | No |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Briqueterie | CM111S2235 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [17 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Buea | CM111S2402 | NA | Yes | No | No | No | No | Yes | Yes | No |  |  | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Buea road | CM111S2294 | NA | Yes | No | No | No | No | Yes | Yes | Yes | No | Yes | Yes |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | No | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | No |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | No | [18 empty] | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Carrefour z | CM111S2274 | NA | Yes | No | No | No | Yes | Yes | No | Yes | Yes | No | No |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre commercial | CM111S2347 | NA | No | No | No | No | No | No | No | No |  |  | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | No |  |  |  | No | Yes | No | No |  | Yes | No | No | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre mbalmayo | CM111S2208 | NA | No | No | No | No | No | No | No | No |  |  | No |  | No |  | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | Yes | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [24 empty] | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Yes |  |  |  | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | No | [7 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Centre n'dere | CM111S2307 | NA | No | No | No | No | No | No | No | No |  |  | No |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | Yes | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | [25 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  |  | No |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  |  |  | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No
AFR | AFO | TotalEnergies Marketing Cameroun S.A | Chefferie bafoussam | CM111S2322 | NA | No | No | No | No | Yes | Yes | No | No |  |  | No |  | No |  | No |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  | No | No | [18 empty] | No | Yes |  |  |  | Yes | Yes | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | [28 empty] | No | [12 empty] | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | No | No | [25 empty] | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No |  | No |  |  |  | Yes |  |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No |  |  |  |  | No